## Project_Areas_WWOL_Master
UID | Name | Details | Status | RelavantLink_1 | RelavantLink_2 | RelevantLink_3 | Census_tract | island | Priority_1_Cesspool_Count | Priority_2_Cesspool_Count | Priority_3_Cesspool_Count | Total_Cesspools | W_in_2_miles_service_area | WWTP_Capacity | WWTP_1_Name | WWTP_2_Name | Total_N_load_kg_yr | Flow_rt | Cost_symbol | Collection_Length_ft | Conveyance_Length_ft | New_WWTP_Needed | WWTP_Upgrade_Needed | Neighborhood_Pump_Stations | Regional_Pump_Stations
H-1 | Pahala | Construction has been started on this project. A Notice to Proceed for the construction of the Pāhala Wastewater Treatment Plant was issued on March 6, 2026. See relevant document(s) below. | Planned or Underway (P) | https://go.hawaii.edu/mXi |  |  | Kau | Hawaii | 0 | 0 | 58 | 58 | Yes, County | Limited Capacity | Pahala WWTP |  | 2204 | 26100 | (4) - $$$$ | 10710.6829 | 222 | Y | N | 0 | 0
H-10 | Wainaku | This project area is within 2 miles of the existing municipal Hilo wastewater service area. There are currently no Hawaiʻi County plans to extend service to this area. However, the Hilo WWTP may have limited available capacity to serve all or part of the project area, depending on how capacity is allocated among future connections in surrounding areas. See relevant document(s) below. | No Active Plans (N) | https://go.hawaii.edu/XXi |  |  | Hilo: Upper Waiakea Forest Reserve | Hawaii | 0 | 0 | 166 | 166 | Yes, County | Limited Capacity | Hilo WWTP |  | 6308 | 74700 | (3) - $$$ | 9197.9095 | 2232 | N | N | 4 | 2
H-11 | Kaūmana | This project area is within 2 miles of the existing municipal Hilo wastewater service area. There are currently no Hawaiʻi County plans to extend service to this area. However, the Hilo WWTP may have limited available capacity to serve all or part of the project area, depending on how capacity is allocated among future connections in surrounding areas. See relevant document(s) below. | No Active Plans (N) | https://go.hawaii.edu/XXi |  |  | Hilo: Kahuku-Kaumana | Hawaii | 0 | 0 | 305 | 305 | Yes, County | Limited Capacity | Hilo WWTP |  | 11590 | 137250 | (4) - $$$$ | 31372.1408 | 5280 | N | N | 6 | 2
H-12 | West Hilo | This project area is within 2 miles of the existing municipal Hilo wastewater service area. There are currently no Hawaiʻi County plans to extend service to this area. However, the Hilo WWTP may have limited available capacity to serve all or part of the project area, depending on how capacity is allocated among future connections in surrounding areas. See relevant document(s) below. | No Active Plans (N) | https://go.hawaii.edu/XXi |  |  | Hilo: Piihonua-Kaumana | Hawaii | 0 | 0 | 1919 | 1919 | Yes, County | Limited Capacity | Hilo WWTP |  | 72922 | 863550 | (3) - $$$ | 150478.9296 | 108 | N | N | 29 | 10
H-13 | Hilo | This project area is within 2 miles of the existing municipal Hilo wastewater service area. There are currently no Hawaiʻi County plans to extend service to this area. However, the Hilo WWTP may have limited available capacity to serve all or part of the project area, depending on how capacity is allocated among future connections in surrounding areas. See relevant document(s) below. | No Active Plans (N) | https://go.hawaii.edu/XXi |  |  | Hilo: Villa Franca-Kaikoo | Hawaii | 0 | 198 | 0 | 198 | Yes, County | Limited Capacity | Hilo WWTP |  | 7524 | 89100 | (3) - $$$ | 15092.0541 | 1046 | N | N | 3 | 1
H-14 | South Hilo | This project area is within 2 miles of the existing municipal Hilo wastewater service area. There are currently no Hawaiʻi County plans to extend service to this area. However, the Hilo WWTP may have limited available capacity to serve all or part of the project area, depending on how capacity is allocated among future connections in surrounding areas. See relevant document(s) below. | No Active Plans (N) | https://go.hawaii.edu/XXi |  |  | Hilo: Puainako | Hawaii | 0 | 737 | 4469 | 5206 | Yes, County | Limited Capacity | Hilo WWTP |  | 197828 | 2342700 | (3) - $$$ | 421364.2409 | 1941 | N | N | 64 | 23
H-15 | Keaukaha | This project area is within 2 miles of the existing municipal Hilo wastewater service area. There are currently no Hawaiʻi County plans to extend service to this area. However, the Hilo WWTP may have limited available capacity to serve all or part of the project area, depending on how capacity is allocated among future connections in surrounding areas. See relevant document(s) below. | No Active Plans (N) | https://go.hawaii.edu/XXi |  |  | Hilo: Keaukaha-Panaewa | Hawaii | 0 | 189 | 0 | 189 | Yes, County | Limited Capacity | Hilo WWTP |  | 7182 | 85050 | (3) - $$$ | 19051.2107 | 501 | N | N | 0 | 0
H-16 | Kuakini Heights | This project area is within 2 miles of the existing municipal Kealakehe wastewater service area and a private wastewater service area. There are currently no Hawaiʻi County or private-sector plans to extend wastewater service to this area. However, the Kealakehe WWTP may have limited available capacity to serve all or part of the project area, depending on how capacity is allocated among future connections in surrounding areas. See relevant document(s) below. | No Active Plans (N) | https://go.hawaii.edu/XXi |  |  | Kahalu'u Mauka | Hawaii | 0 | 148 | 0 | 148 | Yes, County | Limited Capacity | Kealakehe |  | 5624 | 66600 | (3) - $$$ | 8270.3801 | 2685 | N | N | 1 | 1
H-17 | Holualoa | This project area is within 2 miles of the existing municipal Kealakehe wastewater service area and a private wastewater service area. There are currently no Hawaiʻi County or private-sector plans to extend wastewater service to this area. However, the Kealakehe WWTP may have limited available capacity to serve all or part of the project area, depending on how capacity is allocated among future connections in surrounding areas. See relevant document(s) below. | No Active Plans (N) | https://go.hawaii.edu/XXi |  |  | Holualoa | Hawaii | 1543 | 5 | 1 | 1549 | Yes, County | Limited Capacity | Kealakehe |  | 58862 | 697050 | (3) - $$$ | 105383.701 | 461 | N | N | 19 | 7
H-18 | Hawaiian Beaches | This project area is not within 2 miles of an existing wastewater service area but has been identified in the Puna Wastewater Facilities Plan as a potential project area. See relevant document(s) below. | Under Evaluation (E) | https://go.hawaii.edu/2Xi |  |  | Pahoa-Makai | Hawaii | 0 | 0 | 1152 | 1152 | No |  |  |  | 43776 | 518400 | (4) - $$$$ | 207531.9237 | 5280 | Y | N | 18 | 6
H-19 | Nanawele Estates | This project area is not within 2 miles of an existing wastewater service area but has been identified in the Puna Wastewater Facilities Plan as a potential project area. See relevant document(s) below. | Under Evaluation (E) | https://go.hawaii.edu/2Xi |  |  | Pahoa-Makai | Hawaii | 0 | 0 | 213 | 213 | No |  |  |  | 8094 | 95850 | (5) - $$$$$ | 46664.9428 | 5280 | Y | N | 5 | 2
H-2 | Naalehu | This project is in the planned or underway phase. The deadline to close the large capacity cesspools is December 31, 2027. An extension petition is pending County approval. See relevant document(s) below. | Planned or Underway (P) | https://go.hawaii.edu/iXr |  |  | Ka Lae | Hawaii | 0 | 0 | 46 | 46 | Yes, County | Limited Capacity | Naalehu WWTP |  | 1748 | 20700 | (5) - $$$$$ | 10049.7128 | 215 | Y | N | 0 | 1
H-20 | Seaview | This area has no active plans for centralized municipal or private sewer. See relevant document(s) below. | No Active Plans (N) | https://go.hawaii.edu/iXk |  |  | Kalapana-Kapoho | Hawaii | 0 | 0 | 187 | 187 | No |  |  |  | 7106 | 84150 | (5) - $$$$$ | 39802.58 | 5280 | Y | N | 4 | 1
H-21 | Kehena | This area has no active plans for centralized municipal or private sewer. See relevant document(s) below. | No Active Plans (N) | https://go.hawaii.edu/2Xi |  |  | Kalapana-Kapoho | Hawaii | 0 | 0 | 44 | 44 | No |  |  |  | 1672 | 19800 | (5) - $$$$$ | 9795.1163 | 5280 | Y | N | 2 | 1
H-22 | Kaʻohe | This area has no active plans for centralized municipal or private sewer. See relevant document(s) below. | No Active Plans (N) |  |  |  | South Kona | Hawaii | 0 | 0 | 120 | 120 | No |  |  |  | 4560 | 54000 | (5) - $$$$$ | 9502.7232 | 5280 | Y | N | 3 | 1
H-23 | Kīloa | This area has no active plans for centralized municipal or private sewer. See relevant document(s) below. | No Active Plans (N) | https://go.hawaii.edu/XXi |  |  | Konawaena | Hawaii | 0 | 0 | 187 | 187 | No |  |  |  | 7106 | 84150 | (4) - $$$$ | 13700.7487 | 5280 | Y | N | 2 | 1
H-24 | Captain Cook | This area has no active plans for centralized municipal or private sewer. See relevant document(s) below. | No Active Plans (N) | https://go.hawaii.edu/XXi |  |  | Konawaena | Hawaii | 0 | 0 | 110 | 110 | No |  |  |  | 4180 | 49500 | (5) - $$$$$ | 9759.5198 | 5280 | Y | N | 2 | 1
H-25 | Kealakekua | This area has no active plans for centralized municipal or private sewer. See relevant document(s) below. | No Active Plans (N) | https://go.hawaii.edu/XXi |  |  | Konawaena | Hawaii | 0 | 0 | 314 | 314 | Yes, Private | Unknown | Hokuli'a WWTP |  | 11932 | 141300 | (4) - $$$$ | 26330.6457 | 8536 | N | Y | 5 | 2
H-26 | Kalaoa | This area has no active plans for centralized municipal or private sewer. See relevant document(s) below. | No Active Plans (N) |  |  |  | Kalaoa | Hawaii | 0 | 0 | 1616 | 1616 | No |  |  |  | 61408 | 727200 | (4) - $$$$ | 171497.5017 | 5280 | Y | N | 39 | 14
H-27 | Haiwi | This area has no active plans for centralized municipal or private sewer. See relevant document(s) below. | No Active Plans (N) | https://go.hawaii.edu/XXi |  |  | North Kohala | Hawaii | 0 | 0 | 331 | 331 | No |  |  |  | 12578 | 148950 | (4) - $$$$ | 27535.644 | 5280 | Y | N | 6 | 2
H-28 | Kapaau | This area has no active plans for centralized municipal or private sewer. See relevant document(s) below. | No Active Plans (N) | https://go.hawaii.edu/XXi |  |  | North Kohala | Hawaii | 0 | 0 | 222 | 222 | No |  |  |  | 8436 | 99900 | (5) - $$$$$ | 17702.8821 | 5280 | Y | N | 7 | 3
H-29 | Puʻukapu Homesteads | This project area has been identified as a potential project area in the Puakō and South Kohala Regional Wastewater Master Plan. See relevant document(s) below. | Under Evaluation (E) |  |  |  | Waimea - Kohala | Hawaii | 0 | 0 | 181 | 181 | No |  |  |  | 6878 | 81450 | (4) - $$$$ | 12402.537 | 5280 | Y | N | 1 | 1
H-3 | Hillcrest | This project area is within 2 miles of the existing municipal Kealakehe wastewater service area and a private wastewater service area. There are currently no Hawaiʻi County or private-sector plans to extend wastewater service to this area. However, the Kealakehe WWTP may have limited available capacity to serve all or part of the project area, depending on how capacity is allocated among future connections in surrounding areas. See relevant document(s) below. | No Active Plans (N) | https://go.hawaii.edu/XXi |  |  | Pua'a | Hawaii | 88 | 0 | 0 | 88 | Yes, County | Limited Capacity | Kealakehe |  | 3344 | 39600 | (3) - $$$ | 4238.0781 | 354 | N | N | 2 | 1
H-30 | Puʻukapu Homesteads East | This project area has been identified as a potential project area in the Puakō and South Kohala Regional Wastewater Master Plan. See relevant document(s) below. | Under Evaluation (E) |  |  |  | Waimea - Kohala | Hawaii | 0 | 0 | 244 | 244 | No |  |  |  | 9272 | 109800 | (4) - $$$$ | 11485.857 | 5280 | Y | N | 1 | 0
H-31 | Ola Mamalahoa Hwy West | This project area has been identified as a potential project area in the Puakō and South Kohala Regional Wastewater Master Plan. See relevant document(s) below. | Under Evaluation (E) |  |  |  | Waimea - Pu'u Anahulu | Hawaii | 0 | 0 | 253 | 253 | No |  |  |  | 9614 | 113850 | (4) - $$$$ | 14755.9158 | 5280 | Y | N | 2 | 1
H-32 | Paauilo | This area has no active plans for centralized municipal or private sewer. See relevant document(s) below. | No Active Plans (N) | https://go.hawaii.edu/XXi |  |  | Paauhau-Paauilo | Hawaii | 0 | 0 | 139 | 139 | No |  |  |  | 5282 | 62550 | (5) - $$$$$ | 12082.9402 | 5280 | Y | N | 3 | 1
H-33 | Laupahoehoe | This area has no active plans for centralized municipal or private sewer. See relevant document(s) below. | No Active Plans (N) | https://go.hawaii.edu/XXi |  |  | North Hilo | Hawaii | 0 | 0 | 129 | 129 | No |  |  |  | 4902 | 58050 | (4) - $$$$ | 11623.5808 | 5280 | Y | N | 1 | 0
H-34 | Ponahawai | This project area is within 2 miles of the existing municipal Hilo wastewater service area. There are currently no Hawaiʻi County plans to extend service to this area. See relevant document(s) below. | No Active Plans (N) | https://go.hawaii.edu/XXi |  |  | Hilo: Kahuku-Kaumana | Hawaii | 0 | 0 | 129 | 129 | No |  |  |  | 4902 | 58050 | (5) - $$$$$ | 18542.2261 | 5280 | Y | N | 0 | 0
H-35 | Kaūmana Homesteads | This project area is within 2 miles of the existing municipal Hilo wastewater service area. There are currently no Hawaiʻi County plans to extend service to this area. See relevant document(s) below. | No Active Plans (N) | https://go.hawaii.edu/XXi |  |  | Hilo: Kahuku-Kaumana | Hawaii | 0 | 0 | 125 | 125 | No |  |  |  | 4750 | 56250 | (4) - $$$$ | 9422.6305 | 5280 | Y | N | 1 | 0
H-36 | Keaau | This project area is not within 2 miles of an existing wastewater service area but has been identified in the Puna Wastewater Facilities Plan as a potential project area. See relevant document(s) below. | Under Evaluation (E) | https://go.hawaii.edu/2Xi |  |  | Keaau | Hawaii | 0 | 0 | 188 | 188 | No |  |  |  | 7144 | 84600 | (5) - $$$$$ | 26054.3607 | 5280 | Y | N | 6 | 2
H-37 | Mountain View | This project area is not within 2 miles of an existing wastewater service area but has been identified in the Puna Wastewater Facilities Plan as a potential project area. See relevant document(s) below. | Under Evaluation (E) | https://go.hawaii.edu/2Xi |  |  | Volcano-Mt. View | Hawaii | 0 | 0 | 109 | 109 | No |  |  |  | 4142 | 49050 | (5) - $$$$$ | 16259.4049 | 5280 | Y | N | 0 | 0
H-38 | Tiki Gardens | This project area is not within 2 miles of an existing wastewater service area but has been identified in the Puna Wastewater Facilities Plan as a potential project area. See relevant document(s) below. | Under Evaluation (E) | https://go.hawaii.edu/2Xi |  |  | Orchidland-Ainaloa | Hawaii | 0 | 0 | 624 | 624 | No |  |  |  | 23712 | 280800 | (5) - $$$$$ | 130434.6908 | 5280 | Y | N | 6 | 2
H-39 | Waiʻaka | This project area has been identified as a potential project area in the Puakō and South Kohala Regional Wastewater Master Plan. See relevant document(s) below. | Under Evaluation (E) | https://go.hawaii.edu/iXN |  |  | Waimea - Kohala | Hawaii | 10 | 0 | 273 | 283 | Yes, Private | Unknown | Waimea Wastewater Company, Inc. |  | 10754 | 127350 | (5) - $$$$$ | 25633.3587 | 11216 | N | Y | 5 | 2
H-4 | Kailua-Kona | This project area is within 2 miles of the existing municipal Kealakehe wastewater service area and a private wastewater service area. There are currently no Hawaiʻi County or private-sector plans to extend wastewater service to this area. However, the Kealakehe WWTP may have limited available capacity to serve all or part of the project area, depending on how capacity is allocated among future connections in surrounding areas. See relevant document(s) below. | No Active Plans (N) | https://go.hawaii.edu/XXi |  |  | Kailua | Hawaii | 680 | 0 | 0 | 680 | Yes, County | Limited Capacity | Kealakehe |  | 25840 | 306000 | (3) - $$$ | 46709.2067 | 3783 | N | N | 13 | 5
H-40 | Waimea | This project area has been identified as a potential project area in the Puakō and South Kohala Regional Wastewater Master Plan. See relevant document(s) below. | Under Evaluation (E) | https://go.hawaii.edu/iXN |  |  | Waimea - Pu'u Anahulu | Hawaii | 0 | 0 | 585 | 585 | Yes, Private | Unknown | Waimea Wastewater Company, Inc. |  | 22230 | 263250 | (4) - $$$$ | 69377.458 | 10 | N | Y | 9 | 3
H-41 | East Waimea | This project area has been identified as a potential project area in the Puakō and South Kohala Regional Wastewater Master Plan. See relevant document(s) below. | Under Evaluation (E) | https://go.hawaii.edu/iXN |  |  | Waimea - Kohala | Hawaii | 0 | 0 | 225 | 225 | Yes, Private | Unknown | Waimea Wastewater Company, Inc. |  | 8550 | 101250 | (5) - $$$$$ | 28577.996 | 6343 | N | Y | 4 | 2
H-42 | Puako | Puako community is pursuing a sewer line connection to a nearby private treatment plant. See relevant document(s) below. | Under Evaluation (E) | https://go.hawaii.edu/iXD |  |  | Kawaihae - Anaeho'omalu | Hawaii | 120 | 0 | 0 | 120 | Yes, Private | Unknown | Kalahuipua'a Lagoons WWTP |  | 4560 | 54000 | (4) - $$$$ | 9897.9787 | 6165 | N | Y | 0 | 0
H-5 | Kealakehe HHL | This project area is within 2 miles of the existing municipal Kealakehe wastewater service area and a private wastewater service area. There are currently no Hawaiʻi County or private-sector plans to extend wastewater service to this area. However, the Kealakehe WWTP may have limited available capacity to serve all or part of the project area, depending on how capacity is allocated among future connections in surrounding areas. See relevant document(s) below. | No Active Plans (N) |  |  |  | Kealakehe | Hawaii | 110 | 393 | 0 | 503 | Yes, County | Limited Capacity | Kealakehe |  | 19114 | 226350 | (2) - $$ | 28340.677 | 32 | N | N | 7 | 3
H-6 | Honokaa | This project area is within 2 miles of the existing municipal Honokaʻa wastewater service area. There are currently no Hawaiʻi County plans to extend service to this area. However, the Honokaa WWTP may have very limited available capacity for less than 200 homes with cesspools, depending on how capacity is allocated among future connections in surrounding areas. See relevant document(s) below. | No Active Plans (N) | https://go.hawaii.edu/XXi |  |  | Honokaa-Kukuihaele | Hawaii | 0 | 0 | 631 | 631 | Yes, County | No | Honokaa WWTP |  | 23978 | 283950 | (4) - $$$$ | 64566.7207 | 15 | N | Y | 13 | 5
H-7 | Paauhau | This project area is within 2 miles of the existing municipal Honokaʻa wastewater service area. There are currently no Hawaiʻi County plans to extend service to this area. However, the Honokaa WWTP may have very limited available capacity for less than 200 homes with cesspools, depending on how capacity is allocated among future connections in surrounding areas. See relevant document(s) below. | No Active Plans (N) | https://go.hawaii.edu/XXi |  |  | Paauhau-Paauilo | Hawaii | 0 | 0 | 115 | 115 | Yes, County | Limited Capacity | Honokaa WWTP |  | 4370 | 51750 | (5) - $$$$$ | 8387.2117 | 11602 | N | N | 1 | 1
H-8 | Honomu | This project area is within 2 miles of the existing municipal Kulaimano wastewater service area. There are currently no Hawaiʻi County plans to extend service to this area. However, the Kulaimano WWTP may have limited available capacity to serve all or part of the project area, depending on how capacity is allocated among future connections in surrounding areas. See relevant document(s) below. | No Active Plans (N) | https://go.hawaii.edu/XXi |  |  | Paukaa-Wailea | Hawaii | 0 | 0 | 202 | 202 | Yes, County | Limited Capacity | Kulaimano |  | 7676 | 90900 | (4) - $$$$ | 13707.9341 | 16335 | N | N | 1 | 1
H-9 | Wainaku West | This project area is within 2 miles of the existing municipal Hilo wastewater service area. There are currently no Hawaiʻi County plans to extend service to this area. However, the Hilo WWTP may have limited available capacity to serve all or part of the project area, depending on how capacity is allocated among future connections in surrounding areas. See relevant document(s) below. | No Active Plans (N) | https://go.hawaii.edu/XXi |  |  | Hilo: Upper Waiakea Forest Reserve | Hawaii | 0 | 0 | 170 | 170 | Yes, County | Limited Capacity | Hilo WWTP |  | 6460 | 76500 | (3) - $$$ | 10628.8035 | 5731 | N | N | 0 | 0
K-1 | Kekaha | According to a 10/8/25 meeting with the Kauai Division of Wastewater Management, the county identifies this as one of the highest priority low hanging fruit areas. However, the current wastewater treatment plant lacks capacity and sits in a tsunami zone; relocation may be required. See relevant document(s) below. | No Active Plans (N) | https://go.hawaii.edu/sCm |  |  | Kekaha-Waimea | Kauai | 890 | 0 | 0 | 890 | Yes, County | No | Waimea Wastewater Treatment Plant |  | 33820 | 400500 | (4) - $$$$ | 69325.7962 | 4507 | N | Y | 2 | 1
K-10 | Puhi | According to a 10/8/25 meeting with the Kauai Division of Wastewater Management, this area is within 2 miles of the county wastewater service area, but geographic boundaries prevent the expansion of county sewer service to this area. The project area is also within 2 miles of a private wastewater service area. See relevant document(s) below. | No Active Plans (N) | https://go.hawaii.edu/sCm | https://go.hawaii.edu/9Xi |  | Hanamaulu-Lower Puhi | Kauai | 0 | 257 | 0 | 257 | Yes, Private | No | Lihue-Puhi Wastewater Facility |  | 9766 | 115650 | (3) - $$$ | 15037.1823 | 31 | N | Y | 3 | 1
K-11 | Haena | There are currently no plans for centralized sewer service; however, the area's density supports consideration of centralized wastewater infrastructure. See relevant document(s) below. | No Active Plans (N) | https://go.hawaii.edu/sCm |  |  | Haena-Hanalei | Kauai | 122 | 0 | 0 | 122 | No |  |  |  | 4636 | 54900 | (4) - $$$$ | 10421.0583 | 5280 | Y | N | 0 | 0
K-12 | Kilauea | There are currently no plans for centralized sewer service; however, the area's density supports consideration of centralized wastewater infrastructure. See relevant document(s) below. | No Active Plans (N) | https://go.hawaii.edu/sCm | https://go.hawaii.edu/iXc |  | Kalihiwai-Kilauea | Kauai | 0 | 0 | 572 | 572 | No |  |  |  | 21736 | 257400 | (4) - $$$$ | 37704.2982 | 5280 | Y | N | 10 | 4
K-13 | Kipuka St | There are currently no known plans for centralized sewer service; however, the area's density supports consideration of centralized wastewater infrastructure. See relevant document(s) below. | No Active Plans (N) | https://go.hawaii.edu/sCm |  |  | Koloa-Poipu | Kauai | 0 | 77 | 0 | 77 | Yes, Private | Yes | Poipu Wastewater Reclamation Facility | Hyatt Regency Kauai - Grand Hyatt | 2926 | 34650 | (3) - $$$ | 4300.4516 | 1697 | N | N | 1 | 0
K-14 | Hoona Rd | There are currently no known plans for centralized sewer service; however, the area's density supports consideration of centralized wastewater infrastructure. See relevant document(s) below. | No Active Plans (N) | https://go.hawaii.edu/sCm |  |  | Omao-Kukuiula | Kauai | 0 | 3 | 61 | 64 | Yes, Private | Yes | Poipu Wastewater Reclamation Facility |  | 2432 | 28800 | (3) - $$$ | 4118.1488 | 1907 | N | N | 0 | 0
K-15 | Koloa | There are currently no known plans for centralized sewer service; however, the area's density supports consideration of centralized wastewater infrastructure. See relevant document(s) below. | No Active Plans (N) | https://go.hawaii.edu/sCm |  |  | Koloa-Poipu | Kauai | 0 | 343 | 5 | 348 | Yes, Private | Yes | Poipu Wastewater Reclamation Facility |  | 13224 | 156600 | (3) - $$$ | 30337.7942 | 402 | N | N | 3 | 1
K-16 | Omao | There are currently no plans for centralized sewer service; however, the area's density supports consideration of centralized wastewater infrastructure. Despite the project area's proximity to an existing private wastewater service area, its size and geographic boundaries indicate connection to this existing system may be infeasible. See relevant document(s) below. | No Active Plans (N) | https://go.hawaii.edu/sCm | https://go.hawaii.edu/gXi |  | Omao-Kukuiula | Kauai | 0 | 0 | 231 | 231 | Yes, Private | Yes | Poipu Wastewater Reclamation Facility |  | 8778 | 103950 | (4) - $$$$ | 13932.4395 | 13997 | N | N | 4 | 2
K-17 | Lawai | There are currently no plans for centralized sewer service; however, the area's density supports consideration of centralized wastewater infrastructure. Despite the project area's proximity to an existing private wastewater service area, its size and geographic boundaries indicate connection to this existing system may be infeasible. See relevant document(s) below. | No Active Plans (N) | https://go.hawaii.edu/sCm | https://go.hawaii.edu/gXi |  | Omao-Kukuiula | Kauai | 0 | 0 | 520 | 520 | Yes, Private | Yes | Poipu Wastewater Reclamation Facility |  | 19760 | 234000 | (4) - $$$$ | 45021.0449 | 16928 | N | N | 11 | 4
K-18 | Anahola | This project area is on DHHL Land and not in proximity to an exister centralized sewer system. There are historical documents that support feasibility of centralized treatment. See relevant document(s) below. | No Active Plans (N) | https://go.hawaii.edu/FFm |  |  | Anahola | Kauai | 0 | 201 | 0 | 201 | No |  |  |  | 7638 | 90450 | (5) - $$$$$ | 24848.5832 | 5280 | Y | N | 3 | 1
K-19 | Kalaheo | There are currently no plans for centralized sewer service; however, the area's density supports consideration of centralized wastewater infrastructure. Despite the project area's proximity to an existing private wastewater service area, its size and geographic boundaries indicate connection to this existing system may be infeasible. See relevant document(s) below. | No Active Plans (N) | https://go.hawaii.edu/sCm |  |  | Kalaheo-Kalawai Park | Kauai | 0 | 0 | 1325 | 1325 | No |  |  |  | 50350 | 596250 | (4) - $$$$ | 91850.2968 | 5280 | Y | N | 29 | 10
K-2 | Kapaa/Kawaihau | According to a 10/8/25 meeting with the Kauai Division of Wastewater Management, the density of this area merits connection and could be technically feasible, but may not be economically feasible. The Wailua WWTP is in a tsunami zone and may be relocated before additional collection to this plant can be considered. See relevant document(s) below. | No Active Plans (N) | https://go.hawaii.edu/sCm | https://go.hawaii.edu/iX6 |  | Kapaa Town | Kauai | 0 | 1793 | 0 | 1793 | Yes, County | No | Wailua WWTP |  | 68134 | 806850 | (3) - $$$ | 102631.3409 | 5 | N | Y | 25 | 9
K-20 | Hanalei | The Hanalei Initiative has completed a USDA-funded feasibility study evaluating area-wide wastewater options for Hanalei’s remaining cesspools and older septic systems. The effort has now moved into the next planning phase, with the Hanalei Initiative working with EPA to begin a Preliminary Engineering Report for a liquid pressure sewer system. According to a 10/8/25 meeting with the Kauai Division of Wastewater Management, there could be significant groundwater and shoreline constraints if there were to be a project in this area. See relevant document(s) below. | Under Evaluation (E) | https://go.hawaii.edu/sCm | https://www.hanaleiinitiative.org/water-quality |  | Haena-Hanalei | Kauai | 204 | 0 | 0 | 204 | Yes, Private | Unknown | Princeville Resort |  | 7752 | 91800 | (4) - $$$$ | 17625.3433 | 14181 | N | Y | 1 | 0
K-21 | Hanapepe | According to a 10/8/25 meeting with the Kauai Division of Wastewater Management, this area may be able to be connected to county sewer in the future, however, there are no current plans. See relevant document(s) below. | No Active Plans (N) |  |  |  | Kaumakani-Hanapepe | Kauai | 0 | 0 | 339 | 339 | Yes, County | Yes | Eleele WWTP |  | 12882 | 152550 | (1) - $ | 10287.4455 | 91 | N | N | 1 | 0
K-3 | Apopo Rd | According to a 10/8/25 meeting with the Kauai Division of Wastewater Management, the density of this area merits connection and could be technically feasible, but may not be economically feasible. The Wailua WWTP is in a tsunami zone and may be relocated before additional collection to this plant can be considered. See relevant document(s) below. | No Active Plans (N) | https://go.hawaii.edu/sCm | https://go.hawaii.edu/iX6 |  | Kapahi | Kauai | 0 | 55 | 0 | 55 | Yes, County | Yes | Wailua WWTP |  | 2090 | 24750 | (4) - $$$$ | 4813.3995 | 510 | N | N | 1 | 1
K-4 | Kapaa | According to a 10/8/25 meeting with the Kauai Division of Wastewater Management, the density of this area merits connection and could be technically feasible, but may not be economically feasible. The Wailua WWTP is in a tsunami zone and may be relocated before additional collection to this plant can be considered. See relevant document(s) below. | No Active Plans (N) | https://go.hawaii.edu/sCm | https://go.hawaii.edu/iX6 |  | Kapaa Town | Kauai | 0 | 237 | 0 | 237 | Yes, County | Yes | Wailua WWTP |  | 9006 | 106650 | (3) - $$$ | 25390.0566 | 122 | N | N | 0 | 1
K-5 | Wailua | According to a 10/8/25 meeting with the Kauai Division of Wastewater Management, the density of this area merits connection. The Wailua WWTP is in a tsunami zone and may be relocated before additional collection to this plant can be considered. See relevant document(s) below. | No Active Plans (N) | https://go.hawaii.edu/sCm | https://go.hawaii.edu/iX6 |  | Wailua Homesteads | Kauai | 652 | 0 | 0 | 652 | Yes, County | Yes | Wailua WWTP |  | 24776 | 293400 | (2) - $$ | 37298.9853 | 347 | N | N | 8 | 3
K-6 | Olohena | According to a 10/8/25 meeting with the Kauai Division of Wastewater Management, this area may be feasible for a regional facility, however, there are no current plans. The closest existing plant: Wailua WWTP is in a tsunami zone and may be relocated before additional collection to this plant can be considered. See relevant document(s) below. | No Active Plans (N) | https://go.hawaii.edu/sCm |  |  | Wailua Homesteads | Kauai | 149 | 36 | 0 | 185 | Yes, County | Yes | Wailua WWTP |  | 7030 | 83250 | (4) - $$$$ | 11458.5852 | 16732 | N | N | 2 | 1
K-7 | Wailua Homesteads | According to a 10/8/25 meeting with the Kauai Division of Wastewater Management, this area may be feasible for a regional facility, however, there are no current plans. The closest existing plant: Wailua WWTP is in a tsunami zone and may be relocated before additional collection to this plant can be considered. See relevant document(s) below. | No Active Plans (N) | https://go.hawaii.edu/sCm |  |  | Wailua Houselots | Kauai | 325 | 584 | 0 | 909 | Yes, County | No | Wailua WWTP |  | 34542 | 409050 | (4) - $$$$ | 56169.6832 | 10378 | N | Y | 17 | 6
K-8 | Lihue | According to a 10/8/25 meeting with the Kauai Division of Wastewater Management, this area may be able to be connected to county sewer in the future, however, there are no current plans. See relevant document(s) below. | No Active Plans (N) | https://go.hawaii.edu/sCm |  |  | Lihue | Kauai | 0 | 70 | 0 | 70 | Yes, County & Private | No | Lihue Wastewater Treatment Plant |  | 2660 | 31500 | (4) - $$$$ | 5008.5801 | 258 | N | Y | 1 | 1
K-9 | Pua Loke, Ulu Mahi, Ulu Ko | According to a 10/8/25 meeting with the Kauai Division of Wastewater Management, this area is within 2 miles of the county wastewater service area, but geographic boundaries prevent the expansion of county sewer service to this area. The project area is also within 2 miles of the private Lihue-Puhi wastewater service area. See relevant document(s) below. | No Active Plans (N) | https://go.hawaii.edu/sCm |  |  | Lihue | Kauai | 0 | 348 | 0 | 348 | Yes, Private | Unknown | Lihue-Puhi Wastewater Facility |  | 13224 | 156600 | (4) - $$$$ | 19579.5012 | 88 | N | Y | 6 | 2
M-1 | Waikapu | Based on a March 2026 meeting with the Maui County Department of Environmental Management, there are two projects under design and planned for county sewer service in this area. A Maui County study will be conducted to determine additional capacity at the Wailuku-Kahului WWTP. A Central Maui Wastewater Reclamation Facility is also planned. See relevant document(s) below. | Planned or Underway (P) | https://go.hawaii.edu/mCw | https://go.hawaii.edu/iXi |  | Waihee-Waikapu | Maui | 0 | 125 | 0 | 125 | Yes, County | No | Wailuku-Kahului |  | 4750 | 56250 | (3) - $$$ | 9629.5953 | 45 | N | Y | 0 | 0
M-10 | Haiku | Based on an October 2025 meeting with the Maui County Department of Environmental Management, this area is low density and potentially suited only for decentralized or on-site systems See relevant document(s) below. | No Active Plans (N) | https://go.hawaii.edu/mCw |  |  | East Haiku | Maui | 0 | 0 | 253 | 253 | No |  |  |  | 9614 | 113850 | (4) - $$$$ | 21694.8515 | 5280 | Y | N | 1 | 1
M-11 | East Haiku | Based on an October 2025 meeting with the Maui County Department of Environmental Management, this area is low density and potentially suited only for decentralized or on-site systems See relevant document(s) below. | No Active Plans (N) | https://go.hawaii.edu/mCw |  |  | East Haiku | Maui | 0 | 0 | 99 | 99 | No |  |  |  | 3762 | 44550 | (5) - $$$$$ | 7152.2563 | 5280 | Y | N | 3 | 1
M-12 | Hana | This area is not in proximity to county or private systems and is potentially suited only for decentralized or on-site systems See relevant document(s) below. | No Active Plans (N) | https://go.hawaii.edu/mCw |  |  | Hana | Maui | 0 | 0 | 108 | 108 | No |  |  |  | 4104 | 48600 | (5) - $$$$$ | 7461.9548 | 5280 | Y | N | 2 | 1
M-13 | Paʻuwela | Based on an October 2025 meeting with the Maui County Department of Environmental Management, this area is low density and potentially suited only for decentralized or on-site systems See relevant document(s) below. | No Active Plans (N) | https://go.hawaii.edu/mCw |  |  | East Haiku | Maui | 0 | 0 | 108 | 108 | No |  |  |  | 4104 | 48600 | (5) - $$$$$ | 11557.9547 | 5280 | Y | N | 1 | 1
M-14 | Pukalani | The surrounding area is served by a private system (Hawaiʻi Water Service). Maui County is not involved. Private package plant, there is likely a limited incentive to expand service area. See relevant document(s) below. | No Active Plans (N) | https://go.hawaii.edu/mCw |  |  | Pukalani | Maui | 0 | 0 | 1207 | 1207 | Yes, Private | No | Pukalani WWTP |  | 45866 | 543150 | (4) - $$$$ | 116827.1458 | 5280 | N | Y | 17 | 6
M-15 | Makawao | Based on an October 2025 meeting with the Maui County Department of Environmental Management, the county did a rough study ~6–7 yrs ago ($300–400 M, now likely double) $600M+, not published. See relevant document(s) below. | No Active Plans (N) | https://go.hawaii.edu/mCw |  |  | Makawao | Maui | 0 | 0 | 1802 | 1802 | Yes, Private | No | Pukalani WWTP |  | 68476 | 810900 | (3) - $$$ | 113354.6424 | 7872 | N | Y | 22 | 8
M-2 | Old Wailuku Heights | Based on a March 2026 meeting with the Maui County Department of Environmental Management, this project area is under evaluation and is in the CIP 5+ years from now, however, steep slope and terrain conditions may pose challenges. A Maui County study will be conducted to determine additional capacity at the Wailuku-Kahului WWTP. A Central Maui Wastewater Reclamation Facility is also planned. See relevant document(s) below. | Under Evaluation (E) | https://go.hawaii.edu/mCw | https://go.hawaii.edu/iXi |  | Kamaile St. | Maui | 0 | 0 | 58 | 58 | Yes, County | No | Wailuku-Kahului |  | 2204 | 26100 | (3) - $$$ | 3379.6431 | 405 | N | Y | 0 | 0
M-3 | Waihee | Based on a March 2026 meeting with Maui County Department of Environmental Management, this project area is being looked at by an in-house study. It is not currently in any plan. A Maui County study will be conducted to determine additional capacity at the Wailuku-Kahului WWTP. A Central Maui Wastewater Reclamation Facility is also planned. See relevant document(s) below. | Under Evaluation (E) | https://go.hawaii.edu/mCw | https://go.hawaii.edu/iXi |  | Waihee-Waikapu | Maui | 0 | 79 | 0 | 79 | Yes, County | No | Wailuku-Kahului |  | 3002 | 35550 | (3) - $$$ | 4088.5759 | 903 | N | Y | 1 | 0
M-4 | Wahikuli | Based on a March 2026 meeting with Maui County Department of Environmental Management, this project area has been studied through an EPA-funded project, however, the project is not currently funded. The Lahaina WWTP has capacity, however NPDES permit discussions may not allow the connection of more homes at this time. See relevant document(s) below. | Under Evaluation (E) | https://go.hawaii.edu/mCw |  |  | Kahoma | Maui | 212 | 0 | 0 | 212 | Yes, County | Yes | Lahaina WWTP |  | 8056 | 95400 | (1) - $ | 10316.043 | 90 | N | N | 0 | 0
M-5 | Pakele Place | Based on a March 2026 meeting with Maui County Department of Environmental Management, this project area has been identified as a potential area to be connected to county sewer. An in-house study has been conducted. A Maui County study will be conducted to determine additional capacity at the Wailuku-Kahului WWTP. A Central Maui Wastewater Reclamation Facility is also planned. See relevant document(s) below. | Under Evaluation (E) | https://go.hawaii.edu/mCw | https://go.hawaii.edu/iXi |  | North Wailuku | Maui | 0 | 7 | 0 | 7 | Yes, County | Yes | Wailuku-Kahului |  | 266 | 3150 | (4) - $$$$ | 472.844 | 250 | N | N | 1 | 0
M-6 | Waikapu-North | Based on a March 2026 meeting with the Maui County Department of Environmental Management, the county does not have plans for a project in this area. A Maui County study will be conducted to determine additional capacity at the Wailuku-Kahului WWTP. A Central Maui Wastewater Reclamation Facility is also planned. See relevant document(s) below. | No Active Plans (N) | https://go.hawaii.edu/mCw | https://go.hawaii.edu/iXi |  | Waihee-Waikapu | Maui | 0 | 8 | 0 | 8 | Yes, County | Yes | Wailuku-Kahului |  | 304 | 3600 | (3) - $$$ | 856.6245 | 169 | N | N | 0 | 0
M-7 | Maui Meadows | Based on a March 2026 meeting with the Maui County Department of Environmental Management, the county is not planning to implement a project in this area. The Kihei WWTP may have some capacity, but vacant properties may be first in line to be connected. See relevant document(s) below. | No Active Plans (N) | https://go.hawaii.edu/mCw | https://go.hawaii.edu/iXR |  | Kula Makai | Maui | 0 | 616 | 0 | 616 | Yes, County & Private | Yes | Kihei WWTP | Makena Resort | 23408 | 277200 | (3) - $$$ | 43613.3601 | 1575 | N | N | 9 | 3
M-8 | Kula | The majority of the Makawao-Pukalani-Kula Community Plan area is served by individual cesspools/septic tanks. It is expected that new developments in the Upcountry area, aside from those in Hāli`imaile, will all be served by septic systems as required by the State Department of Health See relevant document(s) below. | No Active Plans (N) | https://go.hawaii.edu/mCw | https://go.hawaii.edu/iXi |  | Kula | Maui | 0 | 0 | 176 | 176 | No |  |  |  | 6688 | 79200 | (5) - $$$$$ | 25500.7781 | 5280 | Y | N | 5 | 2
M-9 | ʻŌmaʻopio | The majority of the Makawao-Pukalani-Kula Community Plan area is served by individual cesspools/septic tanks. It is expected that new developments in the Upcountry area, aside from those in Hāli`imaile, will all be served by septic systems as required by the State Department of Health See relevant document(s) below. | No Active Plans (N) | https://go.hawaii.edu/mCw | https://go.hawaii.edu/iXi |  | Kula | Maui | 0 | 0 | 209 | 209 | No |  |  |  | 7942 | 94050 | (4) - $$$$ | 17844.5812 | 5280 | Y | N | 3 | 1
Mo-1 | Puili and Pano Pl | Based on an October 2025 meeting with the Maui County Department of Environmental Management, topography prevents county sewer expansion to this area. The closest treatment plant - Kaunakakai WWTP is located in a sea level rise zone and may need to be relocated. See relevant document(s) below. | No Active Plans (N) | https://go.hawaii.edu/mCw | https://go.hawaii.edu/iXK |  | East Molokai | Molokai | 281 | 0 | 0 | 281 | Yes, County | No | Kaunakakai Wastewater Treatment Plant |  | 10678 | 126450 | (4) - $$$$ | 23812.4202 | 4078 | N | Y | 1 | 0
Mo-2 | North Kalae Hwy | Based on an October 2025 meeting with the Maui County Department of Environmental Management, topography prevents county sewer expansion to this area. If connected to the Kualapuu Collection system this area would be treated by the Molokai Ranch Wastewater treatment plant. See relevant document(s) below. | No Active Plans (N) | https://go.hawaii.edu/mCw | https://go.hawaii.edu/iXK |  | West Molokai | Molokai | 0 | 0 | 100 | 100 | Yes, Private | No | Molokai Ranch WWTP |  | 3800 | 45000 | (5) - $$$$$ | 5848.9641 | 13509 | N | Y | 3 | 1
O-1 | Waimanalo Beach | This project area has been identified in the Six-Year CIP and Budget FY 2026-2031. Relevant document (page 224) : https://go.hawaii.edu/m8T. A study for WWTP capacity is underway. See relevant document(s) below. | Under Evaluation (E) | https://go.hawaii.edu/8Xi |  |  | Waimanalo Bay Beach Park | Oahu | 181 | 0 | 0 | 181 | Yes, County | Yes | Waimanalo Wastewater Treatment Plant |  | 6878 | 81450 | (2) - $$ | 11985.1993 | 18 | N | N | 0 | 0
O-10 | Waianae | According to a 10/14/25 meeting with Honolulu ENV, only the subdivision along Piliuka Place was identified through the Waianae Wastewater Facilities Plan as being feasible for a County System. The area that is feasible for a county system will be included in the FY 2027 CIP. A study is being conducted to determine if the Waianae WWTP has capacity for additional homes. See relevant document(s) below. | Under Evaluation (E) | https://go.hawaii.edu/aXi |  |  | Waianae Kai | Oahu | 86 | 102 | 0 | 188 | Yes, County | No | Waianae WWTP |  | 7144 | 84600 | (2) - $$ | 3269.6776 | 89 | N | Y | 1 | 0
O-11 | Ewa Beach | According to a 10/14/25 meeting with Honolulu ENV, ENV is trying to find a way to proceed with the project by addressing community concerns. See relevant document(s) below. | Planned or Underway (P) | https://go.hawaii.edu/8Xi |  |  | Keanui Drive-Hoomahana Street | Oahu | 886 | 0 | 0 | 886 | Yes, County | Yes | Honouliuli WWTP |  | 33668 | 398700 | (1) - $ | 34500.6368 | 25 | N | N | 2 | 1
O-12 | Kaimuki | This project area will be included in the FY 2027 CIP. See relevant document(s) below. | Under Evaluation (E) | https://go.hawaii.edu/iXb |  |  | Kaimuki: Kapiolani Community College | Oahu | 0 | 0 | 58 | 58 | Yes, County | Yes | Sand Island WWTP/Synagro |  | 2204 | 26100 | (1) - $ | 1883.6573 | 79 | N | N | 1 | 0
O-13 | Diamond head - West | According to a 10/14/25 meeting with Honolulu ENV, Project Planning funds are included in Fiscal Year 2025 CIP Budget. Project title "Diamond Head Sewers, Improvement District". Planning contract in process. Relevant document: https://go.hawaii.edu/m8T See relevant document(s) below. | Under Evaluation (E) | https://go.hawaii.edu/8Xi |  |  | Kapiolani Park | Oahu | 25 | 0 | 0 | 25 | Yes, County | Yes | Sand Island WWTP/Synagro |  | 950 | 11250 | (4) - $$$$ | 3593.0923 | 226 | N | N | 2 | 0
O-14 | Diamond head - East | According to a 10/14/25 meeting with Honolulu ENV, Project Planning funds are included in Fiscal Year 2025 CIP Budget. Project title "Diamond Head Sewers, Improvement District". Planning contract in process. Relevant document: https://go.hawaii.edu/m8T See relevant document(s) below. | Under Evaluation (E) | https://go.hawaii.edu/8Xi |  |  | Diamond Head | Oahu | 0 | 139 | 0 | 139 | Yes, County | Yes | Sand Island WWTP/Synagro |  | 5282 | 62550 | (3) - $$$ | 9951.6063 | 131 | N | N | 6 | 2
O-15 | Tantalus | According to a 10/14/25 meeting with Honolulu ENV, an LPSS system is possible but it is very costly so the City will most likely not execute a project in this area unless other regulatory demands on the CIP budget are relaxed. See relevant document(s) below. | No Active Plans (N) | https://go.hawaii.edu/iXb |  |  | Judd Hillside-Lowrey Avenue | Oahu | 74 | 119 | 0 | 193 | Yes, County | Yes | Sand Island WWTP/Synagro |  | 7334 | 86850 | (4) - $$$$ | 28345.0024 | 154 | N | N | 1 | 1
O-16 | Aiea Heights | According to a 5/15/25 meeting with Honolulu ENV, City Council was reviewing the budget for upcoming fiscal year. The project is dependent on future appropriations. The project area is shown in Fiscal Year 2025 CIP Budget to start in a future year. Relevant document: https://go.hawaii.edu/m8T See relevant document(s) below. | Under Evaluation (E) | https://go.hawaii.edu/8Xi |  |  | Aiea Heights | Oahu | 0 | 102 | 0 | 102 | Yes, County | Yes | Sand Island WWTP/Synagro |  | 3876 | 45900 | (3) - $$$ | 6562.0389 | 1253 | N | N | 3 | 1
O-17 | Kahaluu - Kamehameha HWY | According to a 10/14/25 meeting with Honolulu ENV, Project Planning funds for this project area are included in the Fiscal Year 2024 CIP Budget. Project title "Kamehameha Highway Sewers, Improvement District, Kane'ohe". Planning contract underway. Relevant document: https://go.hawaii.edu/m8T See relevant document(s) below. | Under Evaluation (E) | https://go.hawaii.edu/8Xi |  |  | Ahuimanu | Oahu | 0 | 0 | 20 | 20 | Yes, County | Yes | Kailua |  | 760 | 9000 | (2) - $$ | 1454.8837 | 6 | N | N | 0 | 0
O-18 | Kaaawa | According to a 10/14/25 meeting with Honolulu ENV, this project area is too far away from a City & County of Honolulu system. See relevant document(s) below. | No Active Plans (N) | https://go.hawaii.edu/nXi |  |  | Kaaawa | Oahu | 144 | 0 | 0 | 144 | No |  |  |  | 5472 | 64800 | (5) - $$$$$ | 20731.0172 | 5280 | Y | N | 0 | 0
O-19 | Hauula | According to a 10/14/25 meeting with Honolulu ENV, this project area is too far away from a City & County of Honolulu system. See relevant document(s) below. | No Active Plans (N) | https://go.hawaii.edu/nXi |  |  | Hauula | Oahu | 63 | 0 | 0 | 63 | No |  |  |  | 2394 | 28350 | (4) - $$$$ | 3214.4401 | 5280 | Y | N | 0 | 0
O-2 | Kailua | This project area has been identified in the Six-Year CIP and Budget FY 2026-2031. Relevant document (page 222) : https://go.hawaii.edu/m8T See relevant document(s) below. | Under Evaluation (E) | https://go.hawaii.edu/8Xi |  |  | Kalaheo Avenue | Oahu | 127 | 0 | 0 | 127 | Yes, County | Yes | Kailua |  | 4826 | 57150 | (2) - $$ | 9906.3601 | 1059 | N | N | 0 | 0
O-20 | Pupukea | According to a 10/14/25 meeting with Honolulu ENV, this project area is too far away from a City & County of Honolulu system. See relevant document(s) below. | No Active Plans (N) | https://go.hawaii.edu/iXF |  |  | Sunset Beach | Oahu | 425 | 0 | 0 | 425 | No |  |  |  | 16150 | 191250 | (4) - $$$$ | 49514.355 | 5280 | Y | N | 8 | 3
O-21 | Kawailoa | According to a 10/14/25 meeting with Honolulu ENV, this project area is too far away from a City & County of Honolulu system. See relevant document(s) below. | No Active Plans (N) | https://go.hawaii.edu/iXF |  |  | Kawailoa | Oahu | 70 | 0 | 0 | 70 | No |  |  |  | 2660 | 31500 | (4) - $$$$ | 3253.406 | 5280 | Y | N | 1 | 0
O-22 | Waianae Hawaiian Homeland | DHHL sewer connections are identified as a coordination need in the Waiʻanae Sustainable Communities Plan, but no active sewer project is documented. See relevant document(s) below. | No Active Plans (N) | https://github.com/cshuler/WW_Overlay_2024/blob/main/Document_Archive/Planning_Documents/Oahu_County/UID81_WaianaeSust_Communities_Plan_2012.pdf |  |  | Lualualei-Camp Waianae | Oahu | 0 | 99 | 0 | 99 | Yes, County | No | Waianae WWTP |  | 3762 | 44550 | (4) - $$$$ | 11771.5013 | 6 | N | Y | 1 | 0
O-3 | Ahuimanu | Project Planning funds included in the Fiscal Year 2025 CIP Budget. Project title "Kahaluu Sewers, Section 3, Improvement District". Planning contract in process. See relevant document(s) below. | Under Evaluation (E) | https://go.hawaii.edu/8Xi |  |  | Kahaluu-Waikane | Oahu | 0 | 101 | 31 | 132 | Yes, County | Yes | Kailua |  | 5016 | 59400 | (3) - $$$ | 12671.3052 | 112 | N | N | 2 | 1
O-4 | Kahaluu | According to a 10/14/25 meeting with Honolulu ENV, Project Planning funds are included in the Fiscal Year 2025 CIP Budget. Project title "Kahaluu Sewers, Section 3, Improvement District". A planning contract is in process. Northward expansion may be limited. See relevant document(s) below. | Under Evaluation (E) | https://go.hawaii.edu/8Xi | https://go.hawaii.edu/m8T |  | Kahaluu-Waikane | Oahu | 0 | 224 | 0 | 224 | Yes, County | Yes | Kailua |  | 8512 | 100800 | (3) - $$$ | 23830.0341 | 1493 | N | N | 5 | 2
O-5 | North Hauula | According to a 10/14/25 meeting with Honolulu ENV, this project area is too far away from a City & County of Honolulu system. See relevant document(s) below. | No Active Plans (N) | https://go.hawaii.edu/nXi |  |  | Laie | Oahu | 360 | 0 | 0 | 360 | Yes, Private | Unknown | Laie WWTP (BYU-Hawaii) |  | 13680 | 162000 | (4) - $$$$ | 30580.5034 | 9713 | N | Y | 2 | 1
O-6 | Waialua and Haleiwa | According to a 10/14/25 meeting with Honolulu ENV, this area is under review through the "Paalaa Kai Wastewater Facilities Plan". It has not been determined if a County System is feasible. Therefore, a Private System may be needed. See relevant document(s) below. | Under Evaluation (E) | https://go.hawaii.edu/iXF |  |  | Haleiwa | Oahu | 181 | 0 | 0 | 181 | Yes, County | No | Paalaa Kai WWTP |  | 6878 | 81450 | (4) - $$$$ | 12876.7653 | 6045 | N | Y | 1 | 0
O-7 | Waialua | According to a 10/14/25 meeting with Honolulu ENV, this area is under review through the "Paalaa Kai Wastewater Facilities Plan". It has not been determined if a County System is feasible. Therefore, a Private System may be needed. See relevant document(s) below. | Under Evaluation (E) | https://go.hawaii.edu/iXF |  |  | Waialua District Park | Oahu | 335 | 0 | 0 | 335 | Yes, County | No | Paalaa Kai WWTP |  | 12730 | 150750 | (4) - $$$$ | 39004.5738 | 7661 | N | Y | 3 | 1
O-8 | Mokuleia | According to a 10/14/25 meeting with Honolulu ENV, this area is under review through the "Paalaa Kai Wastewater Facilities Plan". It has not been determined if a County System is feasible. Therefore, a Private System may be needed. See relevant document(s) below. | Under Evaluation (E) | https://go.hawaii.edu/iXF |  |  | Mokuleia | Oahu | 396 | 0 | 0 | 396 | Yes, County | No | Paalaa Kai WWTP |  | 15048 | 178200 | (4) - $$$$ | 33560.2474 | 6050 | N | Y | 0 | 0
O-9 | Makaha | This project area will be in the FY 2027 CIP. See relevant document(s) below. | Under Evaluation (E) | https://go.hawaii.edu/aXi |  |  | Makua Valley | Oahu | 77 | 0 | 0 | 77 | Yes, County | No | Waianae WWTP |  | 2926 | 34650 | (4) - $$$$ | 6905.0462 | 2404 | N | Y | 0 | 0
M-16 | Waikapu-South | This area was removed from project area M-1, and identified by Maui County DEM in email communication as separate but potential future project under evaluation that could be constructed after the new Central Maui plant is constructed, estimated to be completed in 2031. | Under Evaluation (E) | https://go.hawaii.edu/mCw | https://go.hawaii.edu/iXi |  | Waihee-Waikapu | Maui | 0 | 36 | 0 | 36 | Yes, County | No | Wailuku-Kahului |  | 1368 | 16200 | (2) - $$ | 2406.2303 | 45 | N | N | 0 | 0

## Details
UID | Name | Details | Status | RelavantLink_1 | RelavantLink_2 | RelevantLink_3
H-1 | Pahala | Construction has been started on this project. A Notice to Proceed for the construction of the Pāhala Wastewater Treatment Plant was issued on March 6, 2026. See relevant document(s) below. | Planned or Underway (P) | https://go.hawaii.edu/mXi
H-10 | Wainaku | This project area is within 2 miles of the existing municipal Hilo wastewater service area. There are currently no Hawaiʻi County plans to extend service to this area. However, the Hilo WWTP may have limited available capacity to serve all or part of the project area, depending on how capacity is allocated among future connections in surrounding areas. See relevant document(s) below. | No Active Plans (N) | https://go.hawaii.edu/XXi
H-11 | Kaūmana | This project area is within 2 miles of the existing municipal Hilo wastewater service area. There are currently no Hawaiʻi County plans to extend service to this area. However, the Hilo WWTP may have limited available capacity to serve all or part of the project area, depending on how capacity is allocated among future connections in surrounding areas. See relevant document(s) below. | No Active Plans (N) | https://go.hawaii.edu/XXi
H-12 | West Hilo | This project area is within 2 miles of the existing municipal Hilo wastewater service area. There are currently no Hawaiʻi County plans to extend service to this area. However, the Hilo WWTP may have limited available capacity to serve all or part of the project area, depending on how capacity is allocated among future connections in surrounding areas. See relevant document(s) below. | No Active Plans (N) | https://go.hawaii.edu/XXi
H-13 | Hilo | This project area is within 2 miles of the existing municipal Hilo wastewater service area. There are currently no Hawaiʻi County plans to extend service to this area. However, the Hilo WWTP may have limited available capacity to serve all or part of the project area, depending on how capacity is allocated among future connections in surrounding areas. See relevant document(s) below. | No Active Plans (N) | https://go.hawaii.edu/XXi
H-14 | South Hilo | This project area is within 2 miles of the existing municipal Hilo wastewater service area. There are currently no Hawaiʻi County plans to extend service to this area. However, the Hilo WWTP may have limited available capacity to serve all or part of the project area, depending on how capacity is allocated among future connections in surrounding areas. See relevant document(s) below. | No Active Plans (N) | https://go.hawaii.edu/XXi
H-15 | Keaukaha | This project area is within 2 miles of the existing municipal Hilo wastewater service area. There are currently no Hawaiʻi County plans to extend service to this area. However, the Hilo WWTP may have limited available capacity to serve all or part of the project area, depending on how capacity is allocated among future connections in surrounding areas. See relevant document(s) below. | No Active Plans (N) | https://go.hawaii.edu/XXi
H-16 | Kuakini Heights | This project area is within 2 miles of the existing municipal Kealakehe wastewater service area and a private wastewater service area. There are currently no Hawaiʻi County or private-sector plans to extend wastewater service to this area. However, the Kealakehe WWTP may have limited available capacity to serve all or part of the project area, depending on how capacity is allocated among future connections in surrounding areas. See relevant document(s) below. | No Active Plans (N) | https://go.hawaii.edu/XXi
H-17 | Holualoa | This project area is within 2 miles of the existing municipal Kealakehe wastewater service area and a private wastewater service area. There are currently no Hawaiʻi County or private-sector plans to extend wastewater service to this area. However, the Kealakehe WWTP may have limited available capacity to serve all or part of the project area, depending on how capacity is allocated among future connections in surrounding areas. See relevant document(s) below. | No Active Plans (N) | https://go.hawaii.edu/XXi
H-18 | Hawaiian Beaches | This project area is not within 2 miles of an existing wastewater service area but has been identified in the Puna Wastewater Facilities Plan as a potential project area. See relevant document(s) below. | Under Evaluation (E) | https://go.hawaii.edu/2Xi
H-19 | Nanawele Estates | This project area is not within 2 miles of an existing wastewater service area but has been identified in the Puna Wastewater Facilities Plan as a potential project area. See relevant document(s) below. | Under Evaluation (E) | https://go.hawaii.edu/2Xi
H-2 | Naalehu | This project is in the planned or underway phase. The deadline to close the large capacity cesspools is December 31, 2027. An extension petition is pending County approval. See relevant document(s) below. | Planned or Underway (P) | https://go.hawaii.edu/iXr
H-20 | Seaview | This area has no active plans for centralized municipal or private sewer. See relevant document(s) below. | No Active Plans (N) | https://go.hawaii.edu/iXk
H-21 | Kehena | This area has no active plans for centralized municipal or private sewer. See relevant document(s) below. | No Active Plans (N) | https://go.hawaii.edu/2Xi
H-22 | Kaʻohe | This area has no active plans for centralized municipal or private sewer. See relevant document(s) below. | No Active Plans (N)
H-23 | Kīloa | This area has no active plans for centralized municipal or private sewer. See relevant document(s) below. | No Active Plans (N) | https://go.hawaii.edu/XXi
H-24 | Captain Cook | This area has no active plans for centralized municipal or private sewer. See relevant document(s) below. | No Active Plans (N) | https://go.hawaii.edu/XXi
H-25 | Kealakekua | This area has no active plans for centralized municipal or private sewer. See relevant document(s) below. | No Active Plans (N) | https://go.hawaii.edu/XXi
H-26 | Kalaoa | This area has no active plans for centralized municipal or private sewer. See relevant document(s) below. | No Active Plans (N)
H-27 | Haiwi | This area has no active plans for centralized municipal or private sewer. See relevant document(s) below. | No Active Plans (N) | https://go.hawaii.edu/XXi
H-28 | Kapaau | This area has no active plans for centralized municipal or private sewer. See relevant document(s) below. | No Active Plans (N) | https://go.hawaii.edu/XXi
H-29 | Puʻukapu Homesteads | This project area has been identified as a potential project area in the Puakō and South Kohala Regional Wastewater Master Plan. See relevant document(s) below. | Under Evaluation (E)
H-3 | Hillcrest | This project area is within 2 miles of the existing municipal Kealakehe wastewater service area and a private wastewater service area. There are currently no Hawaiʻi County or private-sector plans to extend wastewater service to this area. However, the Kealakehe WWTP may have limited available capacity to serve all or part of the project area, depending on how capacity is allocated among future connections in surrounding areas. See relevant document(s) below. | No Active Plans (N) | https://go.hawaii.edu/XXi
H-30 | Puʻukapu Homesteads East | This project area has been identified as a potential project area in the Puakō and South Kohala Regional Wastewater Master Plan. See relevant document(s) below. | Under Evaluation (E)
H-31 | Ola Mamalahoa Hwy West | This project area has been identified as a potential project area in the Puakō and South Kohala Regional Wastewater Master Plan. See relevant document(s) below. | Under Evaluation (E)
H-32 | Paauilo | This area has no active plans for centralized municipal or private sewer. See relevant document(s) below. | No Active Plans (N) | https://go.hawaii.edu/XXi
H-33 | Laupahoehoe | This area has no active plans for centralized municipal or private sewer. See relevant document(s) below. | No Active Plans (N) | https://go.hawaii.edu/XXi
H-34 | Ponahawai | This project area is within 2 miles of the existing municipal Hilo wastewater service area. There are currently no Hawaiʻi County plans to extend service to this area. See relevant document(s) below. | No Active Plans (N) | https://go.hawaii.edu/XXi
H-35 | Kaūmana Homesteads | This project area is within 2 miles of the existing municipal Hilo wastewater service area. There are currently no Hawaiʻi County plans to extend service to this area. See relevant document(s) below. | No Active Plans (N) | https://go.hawaii.edu/XXi
H-36 | Keaau | This project area is not within 2 miles of an existing wastewater service area but has been identified in the Puna Wastewater Facilities Plan as a potential project area. See relevant document(s) below. | Under Evaluation (E) | https://go.hawaii.edu/2Xi
H-37 | Mountain View | This project area is not within 2 miles of an existing wastewater service area but has been identified in the Puna Wastewater Facilities Plan as a potential project area. See relevant document(s) below. | Under Evaluation (E) | https://go.hawaii.edu/2Xi
H-38 | Tiki Gardens | This project area is not within 2 miles of an existing wastewater service area but has been identified in the Puna Wastewater Facilities Plan as a potential project area. See relevant document(s) below. | Under Evaluation (E) | https://go.hawaii.edu/2Xi
H-39 | Waiʻaka | This project area has been identified as a potential project area in the Puakō and South Kohala Regional Wastewater Master Plan. See relevant document(s) below. | Under Evaluation (E) | https://go.hawaii.edu/iXN
H-4 | Kailua-Kona | This project area is within 2 miles of the existing municipal Kealakehe wastewater service area and a private wastewater service area. There are currently no Hawaiʻi County or private-sector plans to extend wastewater service to this area. However, the Kealakehe WWTP may have limited available capacity to serve all or part of the project area, depending on how capacity is allocated among future connections in surrounding areas. See relevant document(s) below. | No Active Plans (N) | https://go.hawaii.edu/XXi
H-40 | Waimea | This project area has been identified as a potential project area in the Puakō and South Kohala Regional Wastewater Master Plan. See relevant document(s) below. | Under Evaluation (E) | https://go.hawaii.edu/iXN
H-41 | East Waimea | This project area has been identified as a potential project area in the Puakō and South Kohala Regional Wastewater Master Plan. See relevant document(s) below. | Under Evaluation (E) | https://go.hawaii.edu/iXN
H-42 | Puako | Puako community is pursuing a sewer line connection to a nearby private treatment plant. See relevant document(s) below. | Under Evaluation (E) | https://go.hawaii.edu/iXD
H-5 | Kealakehe HHL | This project area is within 2 miles of the existing municipal Kealakehe wastewater service area and a private wastewater service area. There are currently no Hawaiʻi County or private-sector plans to extend wastewater service to this area. However, the Kealakehe WWTP may have limited available capacity to serve all or part of the project area, depending on how capacity is allocated among future connections in surrounding areas. See relevant document(s) below. | No Active Plans (N)
H-6 | Honokaa | This project area is within 2 miles of the existing municipal Honokaʻa wastewater service area. There are currently no Hawaiʻi County plans to extend service to this area. However, the Honokaa WWTP may have very limited available capacity for less than 200 homes with cesspools, depending on how capacity is allocated among future connections in surrounding areas. See relevant document(s) below. | No Active Plans (N) | https://go.hawaii.edu/XXi
H-7 | Paauhau | This project area is within 2 miles of the existing municipal Honokaʻa wastewater service area. There are currently no Hawaiʻi County plans to extend service to this area. However, the Honokaa WWTP may have very limited available capacity for less than 200 homes with cesspools, depending on how capacity is allocated among future connections in surrounding areas. See relevant document(s) below. | No Active Plans (N) | https://go.hawaii.edu/XXi
H-8 | Honomu | This project area is within 2 miles of the existing municipal Kulaimano wastewater service area. There are currently no Hawaiʻi County plans to extend service to this area. However, the Kulaimano WWTP may have limited available capacity to serve all or part of the project area, depending on how capacity is allocated among future connections in surrounding areas. See relevant document(s) below. | No Active Plans (N) | https://go.hawaii.edu/XXi
H-9 | Wainaku West | This project area is within 2 miles of the existing municipal Hilo wastewater service area. There are currently no Hawaiʻi County plans to extend service to this area. However, the Hilo WWTP may have limited available capacity to serve all or part of the project area, depending on how capacity is allocated among future connections in surrounding areas. See relevant document(s) below. | No Active Plans (N) | https://go.hawaii.edu/XXi
K-1 | Kekaha | According to a 10/8/25 meeting with the Kauai Division of Wastewater Management, the county identifies this as one of the highest priority low hanging fruit areas. However, the current wastewater treatment plant lacks capacity and sits in a tsunami zone; relocation may be required. See relevant document(s) below. | No Active Plans (N) | https://go.hawaii.edu/sCm
K-10 | Puhi | According to a 10/8/25 meeting with the Kauai Division of Wastewater Management, this area is within 2 miles of the county wastewater service area, but geographic boundaries prevent the expansion of county sewer service to this area. The project area is also within 2 miles of a private wastewater service area. See relevant document(s) below. | No Active Plans (N) | https://go.hawaii.edu/sCm | https://go.hawaii.edu/9Xi
K-11 | Haena | There are currently no plans for centralized sewer service; however, the area's density supports consideration of centralized wastewater infrastructure. See relevant document(s) below. | No Active Plans (N) | https://go.hawaii.edu/sCm
K-12 | Kilauea | There are currently no plans for centralized sewer service; however, the area's density supports consideration of centralized wastewater infrastructure. See relevant document(s) below. | No Active Plans (N) | https://go.hawaii.edu/sCm | https://go.hawaii.edu/iXc
K-13 | Kipuka St | There are currently no known plans for centralized sewer service; however, the area's density supports consideration of centralized wastewater infrastructure. See relevant document(s) below. | No Active Plans (N) | https://go.hawaii.edu/sCm
K-14 | Hoona Rd | There are currently no known plans for centralized sewer service; however, the area's density supports consideration of centralized wastewater infrastructure. See relevant document(s) below. | No Active Plans (N) | https://go.hawaii.edu/sCm
K-15 | Koloa | There are currently no known plans for centralized sewer service; however, the area's density supports consideration of centralized wastewater infrastructure. See relevant document(s) below. | No Active Plans (N) | https://go.hawaii.edu/sCm
K-16 | Omao | There are currently no plans for centralized sewer service; however, the area's density supports consideration of centralized wastewater infrastructure. Despite the project area's proximity to an existing private wastewater service area, its size and geographic boundaries indicate connection to this existing system may be infeasible. See relevant document(s) below. | No Active Plans (N) | https://go.hawaii.edu/sCm | https://go.hawaii.edu/gXi
K-17 | Lawai | There are currently no plans for centralized sewer service; however, the area's density supports consideration of centralized wastewater infrastructure. Despite the project area's proximity to an existing private wastewater service area, its size and geographic boundaries indicate connection to this existing system may be infeasible. See relevant document(s) below. | No Active Plans (N) | https://go.hawaii.edu/sCm | https://go.hawaii.edu/gXi
K-18 | Anahola | This project area is on DHHL Land and not in proximity to an exister centralized sewer system. There are historical documents that support feasibility of centralized treatment. See relevant document(s) below. | No Active Plans (N) | https://go.hawaii.edu/FFm
K-19 | Kalaheo | There are currently no plans for centralized sewer service; however, the area's density supports consideration of centralized wastewater infrastructure. Despite the project area's proximity to an existing private wastewater service area, its size and geographic boundaries indicate connection to this existing system may be infeasible. See relevant document(s) below. | No Active Plans (N) | https://go.hawaii.edu/sCm
K-2 | Kapaa/Kawaihau | According to a 10/8/25 meeting with the Kauai Division of Wastewater Management, the density of this area merits connection and could be technically feasible, but may not be economically feasible. The Wailua WWTP is in a tsunami zone and may be relocated before additional collection to this plant can be considered. See relevant document(s) below. | No Active Plans (N) | https://go.hawaii.edu/sCm | https://go.hawaii.edu/iX6
K-20 | Hanalei | The Hanalei Initiative has completed a USDA-funded feasibility study evaluating area-wide wastewater options for Hanalei’s remaining cesspools and older septic systems. The effort has now moved into the next planning phase, with the Hanalei Initiative working with EPA to begin a Preliminary Engineering Report for a liquid pressure sewer system. According to a 10/8/25 meeting with the Kauai Division of Wastewater Management, there could be significant groundwater and shoreline constraints if there were to be a project in this area. See relevant document(s) below. | Under Evaluation (E) | https://go.hawaii.edu/sCm | https://www.hanaleiinitiative.org/water-quality
K-21 | Hanapepe | According to a 10/8/25 meeting with the Kauai Division of Wastewater Management, this area may be able to be connected to county sewer in the future, however, there are no current plans. See relevant document(s) below. | No Active Plans (N)
K-3 | Apopo Rd | According to a 10/8/25 meeting with the Kauai Division of Wastewater Management, the density of this area merits connection and could be technically feasible, but may not be economically feasible. The Wailua WWTP is in a tsunami zone and may be relocated before additional collection to this plant can be considered. See relevant document(s) below. | No Active Plans (N) | https://go.hawaii.edu/sCm | https://go.hawaii.edu/iX6
K-4 | Kapaa | According to a 10/8/25 meeting with the Kauai Division of Wastewater Management, the density of this area merits connection and could be technically feasible, but may not be economically feasible. The Wailua WWTP is in a tsunami zone and may be relocated before additional collection to this plant can be considered. See relevant document(s) below. | No Active Plans (N) | https://go.hawaii.edu/sCm | https://go.hawaii.edu/iX6
K-5 | Wailua | According to a 10/8/25 meeting with the Kauai Division of Wastewater Management, the density of this area merits connection. The Wailua WWTP is in a tsunami zone and may be relocated before additional collection to this plant can be considered. See relevant document(s) below. | No Active Plans (N) | https://go.hawaii.edu/sCm | https://go.hawaii.edu/iX6
K-6 | Olohena | According to a 10/8/25 meeting with the Kauai Division of Wastewater Management, this area may be feasible for a regional facility, however, there are no current plans. The closest existing plant: Wailua WWTP is in a tsunami zone and may be relocated before additional collection to this plant can be considered. See relevant document(s) below. | No Active Plans (N) | https://go.hawaii.edu/sCm
K-7 | Wailua Homesteads | According to a 10/8/25 meeting with the Kauai Division of Wastewater Management, this area may be feasible for a regional facility, however, there are no current plans. The closest existing plant: Wailua WWTP is in a tsunami zone and may be relocated before additional collection to this plant can be considered. See relevant document(s) below. | No Active Plans (N) | https://go.hawaii.edu/sCm
K-8 | Lihue | According to a 10/8/25 meeting with the Kauai Division of Wastewater Management, this area may be able to be connected to county sewer in the future, however, there are no current plans. See relevant document(s) below. | No Active Plans (N) | https://go.hawaii.edu/sCm
K-9 | Pua Loke, Ulu Mahi, Ulu Ko | According to a 10/8/25 meeting with the Kauai Division of Wastewater Management, this area is within 2 miles of the county wastewater service area, but geographic boundaries prevent the expansion of county sewer service to this area. The project area is also within 2 miles of the private Lihue-Puhi wastewater service area. See relevant document(s) below. | No Active Plans (N) | https://go.hawaii.edu/sCm
M-1 | Waikapu | Based on a March 2026 meeting with the Maui County Department of Environmental Management, there are two projects under design and planned for county sewer service in this area. A Maui County study will be conducted to determine additional capacity at the Wailuku-Kahului WWTP. A Central Maui Wastewater Reclamation Facility is also planned. See relevant document(s) below. | Planned or Underway (P) | https://go.hawaii.edu/mCw | https://go.hawaii.edu/iXi
M-10 | Haiku | Based on an October 2025 meeting with the Maui County Department of Environmental Management, this area is low density and potentially suited only for decentralized or on-site systems See relevant document(s) below. | No Active Plans (N) | https://go.hawaii.edu/mCw
M-11 | East Haiku | Based on an October 2025 meeting with the Maui County Department of Environmental Management, this area is low density and potentially suited only for decentralized or on-site systems See relevant document(s) below. | No Active Plans (N) | https://go.hawaii.edu/mCw
M-12 | Hana | This area is not in proximity to county or private systems and is potentially suited only for decentralized or on-site systems See relevant document(s) below. | No Active Plans (N) | https://go.hawaii.edu/mCw
M-13 | Paʻuwela | Based on an October 2025 meeting with the Maui County Department of Environmental Management, this area is low density and potentially suited only for decentralized or on-site systems See relevant document(s) below. | No Active Plans (N) | https://go.hawaii.edu/mCw
M-14 | Pukalani | The surrounding area is served by a private system (Hawaiʻi Water Service). Maui County is not involved. Private package plant, there is likely a limited incentive to expand service area. See relevant document(s) below. | No Active Plans (N) | https://go.hawaii.edu/mCw
M-15 | Makawao | Based on an October 2025 meeting with the Maui County Department of Environmental Management, the county did a rough study ~6–7 yrs ago ($300–400 M, now likely double) $600M+, not published. See relevant document(s) below. | No Active Plans (N) | https://go.hawaii.edu/mCw
M-2 | Old Wailuku Heights | Based on a March 2026 meeting with the Maui County Department of Environmental Management, this project area is under evaluation and is in the CIP 5+ years from now, however, steep slope and terrain conditions may pose challenges. A Maui County study will be conducted to determine additional capacity at the Wailuku-Kahului WWTP. A Central Maui Wastewater Reclamation Facility is also planned. See relevant document(s) below. | Under Evaluation (E) | https://go.hawaii.edu/mCw | https://go.hawaii.edu/iXi
M-3 | Waihee | Based on a March 2026 meeting with Maui County Department of Environmental Management, this project area is being looked at by an in-house study. It is not currently in any plan. A Maui County study will be conducted to determine additional capacity at the Wailuku-Kahului WWTP. A Central Maui Wastewater Reclamation Facility is also planned. See relevant document(s) below. | Under Evaluation (E) | https://go.hawaii.edu/mCw | https://go.hawaii.edu/iXi
M-4 | Wahikuli | Based on a March 2026 meeting with Maui County Department of Environmental Management, this project area has been studied through an EPA-funded project, however, the project is not currently funded. The Lahaina WWTP has capacity, however NPDES permit discussions may not allow the connection of more homes at this time. See relevant document(s) below. | Under Evaluation (E) | https://go.hawaii.edu/mCw
M-5 | Pakele Place | Based on a March 2026 meeting with Maui County Department of Environmental Management, this project area has been identified as a potential area to be connected to county sewer. An in-house study has been conducted. A Maui County study will be conducted to determine additional capacity at the Wailuku-Kahului WWTP. A Central Maui Wastewater Reclamation Facility is also planned. See relevant document(s) below. | Under Evaluation (E) | https://go.hawaii.edu/mCw | https://go.hawaii.edu/iXi
M-6 | Waikapu-North | Based on a March 2026 meeting with the Maui County Department of Environmental Management, the county does not have plans for a project in this area. A Maui County study will be conducted to determine additional capacity at the Wailuku-Kahului WWTP. A Central Maui Wastewater Reclamation Facility is also planned. See relevant document(s) below. | No Active Plans (N) | https://go.hawaii.edu/mCw | https://go.hawaii.edu/iXi
M-7 | Maui Meadows | Based on a March 2026 meeting with the Maui County Department of Environmental Management, the county is not planning to implement a project in this area. The Kihei WWTP may have some capacity, but vacant properties may be first in line to be connected. See relevant document(s) below. | No Active Plans (N) | https://go.hawaii.edu/mCw | https://go.hawaii.edu/iXR
M-8 | Kula | The majority of the Makawao-Pukalani-Kula Community Plan area is served by individual cesspools/septic tanks. It is expected that new developments in the Upcountry area, aside from those in Hāli`imaile, will all be served by septic systems as required by the State Department of Health See relevant document(s) below. | No Active Plans (N) | https://go.hawaii.edu/mCw | https://go.hawaii.edu/iXi
M-9 | ʻŌmaʻopio | The majority of the Makawao-Pukalani-Kula Community Plan area is served by individual cesspools/septic tanks. It is expected that new developments in the Upcountry area, aside from those in Hāli`imaile, will all be served by septic systems as required by the State Department of Health See relevant document(s) below. | No Active Plans (N) | https://go.hawaii.edu/mCw | https://go.hawaii.edu/iXi
Mo-1 | Puili and Pano Pl | Based on an October 2025 meeting with the Maui County Department of Environmental Management, topography prevents county sewer expansion to this area. The closest treatment plant - Kaunakakai WWTP is located in a sea level rise zone and may need to be relocated. See relevant document(s) below. | No Active Plans (N) | https://go.hawaii.edu/mCw | https://go.hawaii.edu/iXK
Mo-2 | North Kalae Hwy | Based on an October 2025 meeting with the Maui County Department of Environmental Management, topography prevents county sewer expansion to this area. If connected to the Kualapuu Collection system this area would be treated by the Molokai Ranch Wastewater treatment plant. See relevant document(s) below. | No Active Plans (N) | https://go.hawaii.edu/mCw | https://go.hawaii.edu/iXK
O-1 | Waimanalo Beach | This project area has been identified in the Six-Year CIP and Budget FY 2026-2031. Relevant document (page 224) : https://go.hawaii.edu/m8T. A study for WWTP capacity is underway. See relevant document(s) below. | Under Evaluation (E) | https://go.hawaii.edu/8Xi
O-10 | Waianae | According to a 10/14/25 meeting with Honolulu ENV, only the subdivision along Piliuka Place was identified through the Waianae Wastewater Facilities Plan as being feasible for a County System. The area that is feasible for a county system will be included in the FY 2027 CIP. A study is being conducted to determine if the Waianae WWTP has capacity for additional homes. See relevant document(s) below. | Under Evaluation (E) | https://go.hawaii.edu/aXi
O-11 | Ewa Beach | According to a 10/14/25 meeting with Honolulu ENV, ENV is trying to find a way to proceed with the project by addressing community concerns. See relevant document(s) below. | Planned or Underway (P) | https://go.hawaii.edu/8Xi
O-12 | Kaimuki | This project area will be included in the FY 2027 CIP. See relevant document(s) below. | Under Evaluation (E) | https://go.hawaii.edu/iXb
O-13 | Diamond head - West | According to a 10/14/25 meeting with Honolulu ENV, Project Planning funds are included in Fiscal Year 2025 CIP Budget. Project title "Diamond Head Sewers, Improvement District". Planning contract in process. Relevant document: https://go.hawaii.edu/m8T See relevant document(s) below. | Under Evaluation (E) | https://go.hawaii.edu/8Xi
O-14 | Diamond head - East | According to a 10/14/25 meeting with Honolulu ENV, Project Planning funds are included in Fiscal Year 2025 CIP Budget. Project title "Diamond Head Sewers, Improvement District". Planning contract in process. Relevant document: https://go.hawaii.edu/m8T See relevant document(s) below. | Under Evaluation (E) | https://go.hawaii.edu/8Xi
O-15 | Tantalus | According to a 10/14/25 meeting with Honolulu ENV, an LPSS system is possible but it is very costly so the City will most likely not execute a project in this area unless other regulatory demands on the CIP budget are relaxed. See relevant document(s) below. | No Active Plans (N) | https://go.hawaii.edu/iXb
O-16 | Aiea Heights | According to a 5/15/25 meeting with Honolulu ENV, City Council was reviewing the budget for upcoming fiscal year. The project is dependent on future appropriations. The project area is shown in Fiscal Year 2025 CIP Budget to start in a future year. Relevant document: https://go.hawaii.edu/m8T See relevant document(s) below. | Under Evaluation (E) | https://go.hawaii.edu/8Xi
O-17 | Kahaluu - Kamehameha HWY | According to a 10/14/25 meeting with Honolulu ENV, Project Planning funds for this project area are included in the Fiscal Year 2024 CIP Budget. Project title "Kamehameha Highway Sewers, Improvement District, Kane'ohe". Planning contract underway. Relevant document: https://go.hawaii.edu/m8T See relevant document(s) below. | Under Evaluation (E) | https://go.hawaii.edu/8Xi
O-18 | Kaaawa | According to a 10/14/25 meeting with Honolulu ENV, this project area is too far away from a City & County of Honolulu system. See relevant document(s) below. | No Active Plans (N) | https://go.hawaii.edu/nXi
O-19 | Hauula | According to a 10/14/25 meeting with Honolulu ENV, this project area is too far away from a City & County of Honolulu system. See relevant document(s) below. | No Active Plans (N) | https://go.hawaii.edu/nXi
O-2 | Kailua | This project area has been identified in the Six-Year CIP and Budget FY 2026-2031. Relevant document (page 222) : https://go.hawaii.edu/m8T See relevant document(s) below. | Under Evaluation (E) | https://go.hawaii.edu/8Xi
O-20 | Pupukea | According to a 10/14/25 meeting with Honolulu ENV, this project area is too far away from a City & County of Honolulu system. See relevant document(s) below. | No Active Plans (N) | https://go.hawaii.edu/iXF
O-21 | Kawailoa | According to a 10/14/25 meeting with Honolulu ENV, this project area is too far away from a City & County of Honolulu system. See relevant document(s) below. | No Active Plans (N) | https://go.hawaii.edu/iXF
O-22 | Waianae Hawaiian Homeland | DHHL sewer connections are identified as a coordination need in the Waiʻanae Sustainable Communities Plan, but no active sewer project is documented. See relevant document(s) below. | No Active Plans (N) | https://github.com/cshuler/WW_Overlay_2024/blob/main/Document_Archive/Planning_Documents/Oahu_County/UID81_WaianaeSust_Communities_Plan_2012.pdf
O-3 | Ahuimanu | Project Planning funds included in the Fiscal Year 2025 CIP Budget. Project title "Kahaluu Sewers, Section 3, Improvement District". Planning contract in process. See relevant document(s) below. | Under Evaluation (E) | https://go.hawaii.edu/8Xi
O-4 | Kahaluu | According to a 10/14/25 meeting with Honolulu ENV, Project Planning funds are included in the Fiscal Year 2025 CIP Budget. Project title "Kahaluu Sewers, Section 3, Improvement District". A planning contract is in process. Northward expansion may be limited. See relevant document(s) below. | Under Evaluation (E) | https://go.hawaii.edu/8Xi | https://go.hawaii.edu/m8T
O-5 | North Hauula | According to a 10/14/25 meeting with Honolulu ENV, this project area is too far away from a City & County of Honolulu system. See relevant document(s) below. | No Active Plans (N) | https://go.hawaii.edu/nXi
O-6 | Waialua and Haleiwa | According to a 10/14/25 meeting with Honolulu ENV, this area is under review through the "Paalaa Kai Wastewater Facilities Plan". It has not been determined if a County System is feasible. Therefore, a Private System may be needed. See relevant document(s) below. | Under Evaluation (E) | https://go.hawaii.edu/iXF
O-7 | Waialua | According to a 10/14/25 meeting with Honolulu ENV, this area is under review through the "Paalaa Kai Wastewater Facilities Plan". It has not been determined if a County System is feasible. Therefore, a Private System may be needed. See relevant document(s) below. | Under Evaluation (E) | https://go.hawaii.edu/iXF
O-8 | Mokuleia | According to a 10/14/25 meeting with Honolulu ENV, this area is under review through the "Paalaa Kai Wastewater Facilities Plan". It has not been determined if a County System is feasible. Therefore, a Private System may be needed. See relevant document(s) below. | Under Evaluation (E) | https://go.hawaii.edu/iXF
O-9 | Makaha | This project area will be in the FY 2027 CIP. See relevant document(s) below. | Under Evaluation (E) | https://go.hawaii.edu/aXi
M-16 | Waikapu-South | This area was removed from project area M-1, and identified by Maui County DEM in email communication as separate but potential future project under evaluation that could be constructed after the new Central Maui plant is constructed, estimated to be completed in 2031. | Under Evaluation (E) | https://go.hawaii.edu/mCw | https://go.hawaii.edu/iXi

## Metadata
UID | Census_tract | island | Priority_1_Cesspool_Count | Priority_2_Cesspool_Count | Priority_3_Cesspool_Count | Total_Cesspools | W_in_2_miles_service_area | WWTP_Capacity | WWTP_1_Name | WWTP_2_Name | Total_N_load_kg_yr | Flow_rt_(GPD)
H-1 | Kau | Hawaii | 0 | 0 | 58 | 58 | Yes, County | Limited Capacity | Pahala WWTP |  | 2204 | 26100
H-10 | Hilo: Upper Waiakea Forest Reserve | Hawaii | 0 | 0 | 166 | 166 | Yes, County | Limited Capacity | Hilo WWTP |  | 6308 | 74700
H-11 | Hilo: Kahuku-Kaumana | Hawaii | 0 | 0 | 305 | 305 | Yes, County | Limited Capacity | Hilo WWTP |  | 11590 | 137250
H-12 | Hilo: Piihonua-Kaumana | Hawaii | 0 | 0 | 1919 | 1919 | Yes, County | Limited Capacity | Hilo WWTP |  | 72922 | 863550
H-13 | Hilo: Villa Franca-Kaikoo | Hawaii | 0 | 198 | 0 | 198 | Yes, County | Limited Capacity | Hilo WWTP |  | 7524 | 89100
H-14 | Hilo: Puainako | Hawaii | 0 | 737 | 4469 | 5206 | Yes, County | Limited Capacity | Hilo WWTP |  | 197828 | 2342700
H-15 | Hilo: Keaukaha-Panaewa | Hawaii | 0 | 189 | 0 | 189 | Yes, County | Limited Capacity | Hilo WWTP |  | 7182 | 85050
H-16 | Kahalu'u Mauka | Hawaii | 0 | 148 | 0 | 148 | Yes, County | Limited Capacity | Kealakehe |  | 5624 | 66600
H-17 | Holualoa | Hawaii | 1543 | 5 | 1 | 1549 | Yes, County | Limited Capacity | Kealakehe |  | 58862 | 697050
H-18 | Pahoa-Makai | Hawaii | 0 | 0 | 1152 | 1152 | No |  |  |  | 43776 | 518400
H-19 | Pahoa-Makai | Hawaii | 0 | 0 | 213 | 213 | No |  |  |  | 8094 | 95850
H-2 | Ka Lae | Hawaii | 0 | 0 | 46 | 46 | Yes, County | Limited Capacity | Naalehu WWTP |  | 1748 | 20700
H-20 | Kalapana-Kapoho | Hawaii | 0 | 0 | 187 | 187 | No |  |  |  | 7106 | 84150
H-21 | Kalapana-Kapoho | Hawaii | 0 | 0 | 44 | 44 | No |  |  |  | 1672 | 19800
H-22 | South Kona | Hawaii | 0 | 0 | 120 | 120 | No |  |  |  | 4560 | 54000
H-23 | Konawaena | Hawaii | 0 | 0 | 187 | 187 | No |  |  |  | 7106 | 84150
H-24 | Konawaena | Hawaii | 0 | 0 | 110 | 110 | No |  |  |  | 4180 | 49500
H-25 | Konawaena | Hawaii | 0 | 0 | 314 | 314 | Yes, Private | Unknown | Hokuli'a WWTP |  | 11932 | 141300
H-26 | Kalaoa | Hawaii | 0 | 0 | 1616 | 1616 | No |  |  |  | 61408 | 727200
H-27 | North Kohala | Hawaii | 0 | 0 | 331 | 331 | No |  |  |  | 12578 | 148950
H-28 | North Kohala | Hawaii | 0 | 0 | 222 | 222 | No |  |  |  | 8436 | 99900
H-29 | Waimea - Kohala | Hawaii | 0 | 0 | 181 | 181 | No |  |  |  | 6878 | 81450
H-3 | Pua'a | Hawaii | 88 | 0 | 0 | 88 | Yes, County | Limited Capacity | Kealakehe |  | 3344 | 39600
H-30 | Waimea - Kohala | Hawaii | 0 | 0 | 244 | 244 | No |  |  |  | 9272 | 109800
H-31 | Waimea - Pu'u Anahulu | Hawaii | 0 | 0 | 253 | 253 | No |  |  |  | 9614 | 113850
H-32 | Paauhau-Paauilo | Hawaii | 0 | 0 | 139 | 139 | No |  |  |  | 5282 | 62550
H-33 | North Hilo | Hawaii | 0 | 0 | 129 | 129 | No |  |  |  | 4902 | 58050
H-34 | Hilo: Kahuku-Kaumana | Hawaii | 0 | 0 | 129 | 129 | No |  |  |  | 4902 | 58050
H-35 | Hilo: Kahuku-Kaumana | Hawaii | 0 | 0 | 125 | 125 | No |  |  |  | 4750 | 56250
H-36 | Keaau | Hawaii | 0 | 0 | 188 | 188 | No |  |  |  | 7144 | 84600
H-37 | Volcano-Mt. View | Hawaii | 0 | 0 | 109 | 109 | No |  |  |  | 4142 | 49050
H-38 | Orchidland-Ainaloa | Hawaii | 0 | 0 | 624 | 624 | No |  |  |  | 23712 | 280800
H-39 | Waimea - Kohala | Hawaii | 10 | 0 | 273 | 283 | Yes, Private | Unknown | Waimea Wastewater Company, Inc. |  | 10754 | 127350
H-4 | Kailua | Hawaii | 680 | 0 | 0 | 680 | Yes, County | Limited Capacity | Kealakehe |  | 25840 | 306000
H-40 | Waimea - Pu'u Anahulu | Hawaii | 0 | 0 | 585 | 585 | Yes, Private | Unknown | Waimea Wastewater Company, Inc. |  | 22230 | 263250
H-41 | Waimea - Kohala | Hawaii | 0 | 0 | 225 | 225 | Yes, Private | Unknown | Waimea Wastewater Company, Inc. |  | 8550 | 101250
H-42 | Kawaihae - Anaeho'omalu | Hawaii | 120 | 0 | 0 | 120 | Yes, Private | Unknown | Kalahuipua'a Lagoons WWTP |  | 4560 | 54000
H-5 | Kealakehe | Hawaii | 110 | 393 | 0 | 503 | Yes, County | Limited Capacity | Kealakehe |  | 19114 | 226350
H-6 | Honokaa-Kukuihaele | Hawaii | 0 | 0 | 631 | 631 | Yes, County | No | Honokaa WWTP |  | 23978 | 283950
H-7 | Paauhau-Paauilo | Hawaii | 0 | 0 | 115 | 115 | Yes, County | Limited Capacity | Honokaa WWTP |  | 4370 | 51750
H-8 | Paukaa-Wailea | Hawaii | 0 | 0 | 202 | 202 | Yes, County | Limited Capacity | Kulaimano |  | 7676 | 90900
H-9 | Hilo: Upper Waiakea Forest Reserve | Hawaii | 0 | 0 | 170 | 170 | Yes, County | Limited Capacity | Hilo WWTP |  | 6460 | 76500
K-1 | Kekaha-Waimea | Kauai | 890 | 0 | 0 | 890 | Yes, County | No | Waimea Wastewater Treatment Plant |  | 33820 | 400500
K-10 | Hanamaulu-Lower Puhi | Kauai | 0 | 257 | 0 | 257 | Yes, Private | No | Lihue-Puhi Wastewater Facility |  | 9766 | 115650
K-11 | Haena-Hanalei | Kauai | 122 | 0 | 0 | 122 | No |  |  |  | 4636 | 54900
K-12 | Kalihiwai-Kilauea | Kauai | 0 | 0 | 572 | 572 | No |  |  |  | 21736 | 257400
K-13 | Koloa-Poipu | Kauai | 0 | 77 | 0 | 77 | Yes, Private | Yes | Poipu Wastewater Reclamation Facility | Hyatt Regency Kauai - Grand Hyatt | 2926 | 34650
K-14 | Omao-Kukuiula | Kauai | 0 | 3 | 61 | 64 | Yes, Private | Yes | Poipu Wastewater Reclamation Facility |  | 2432 | 28800
K-15 | Koloa-Poipu | Kauai | 0 | 343 | 5 | 348 | Yes, Private | Yes | Poipu Wastewater Reclamation Facility |  | 13224 | 156600
K-16 | Omao-Kukuiula | Kauai | 0 | 0 | 231 | 231 | Yes, Private | Yes | Poipu Wastewater Reclamation Facility |  | 8778 | 103950
K-17 | Omao-Kukuiula | Kauai | 0 | 0 | 520 | 520 | Yes, Private | Yes | Poipu Wastewater Reclamation Facility |  | 19760 | 234000
K-18 | Anahola | Kauai | 0 | 201 | 0 | 201 | No |  |  |  | 7638 | 90450
K-19 | Kalaheo-Kalawai Park | Kauai | 0 | 0 | 1325 | 1325 | No |  |  |  | 50350 | 596250
K-2 | Kapaa Town | Kauai | 0 | 1793 | 0 | 1793 | Yes, County | No | Wailua WWTP |  | 68134 | 806850
K-20 | Haena-Hanalei | Kauai | 204 | 0 | 0 | 204 | Yes, Private | Unknown | Princeville Resort |  | 7752 | 91800
K-21 | Kaumakani-Hanapepe | Kauai | 0 | 0 | 339 | 339 | Yes, County | Yes | Eleele WWTP |  | 12882 | 152550
K-3 | Kapahi | Kauai | 0 | 55 | 0 | 55 | Yes, County | Yes | Wailua WWTP |  | 2090 | 24750
K-4 | Kapaa Town | Kauai | 0 | 237 | 0 | 237 | Yes, County | Yes | Wailua WWTP |  | 9006 | 106650
K-5 | Wailua Homesteads | Kauai | 652 | 0 | 0 | 652 | Yes, County | Yes | Wailua WWTP |  | 24776 | 293400
K-6 | Wailua Homesteads | Kauai | 149 | 36 | 0 | 185 | Yes, County | Yes | Wailua WWTP |  | 7030 | 83250
K-7 | Wailua Houselots | Kauai | 325 | 584 | 0 | 909 | Yes, County | No | Wailua WWTP |  | 34542 | 409050
K-8 | Lihue | Kauai | 0 | 70 | 0 | 70 | Yes, County & Private | No | Lihue Wastewater Treatment Plant |  | 2660 | 31500
K-9 | Lihue | Kauai | 0 | 348 | 0 | 348 | Yes, Private | Unknown | Lihue-Puhi Wastewater Facility |  | 13224 | 156600
M-1 | Waihee-Waikapu | Maui | 0 | 125 | 0 | 125 | Yes, County | No | Wailuku-Kahului |  | 4750 | 56250
M-10 | East Haiku | Maui | 0 | 0 | 253 | 253 | No |  |  |  | 9614 | 113850
M-11 | East Haiku | Maui | 0 | 0 | 99 | 99 | No |  |  |  | 3762 | 44550
M-12 | Hana | Maui | 0 | 0 | 108 | 108 | No |  |  |  | 4104 | 48600
M-13 | East Haiku | Maui | 0 | 0 | 108 | 108 | No |  |  |  | 4104 | 48600
M-14 | Pukalani | Maui | 0 | 0 | 1207 | 1207 | Yes, Private | No | Pukalani WWTP |  | 45866 | 543150
M-15 | Makawao | Maui | 0 | 0 | 1802 | 1802 | Yes, Private | No | Pukalani WWTP |  | 68476 | 810900
M-2 | Kamaile St. | Maui | 0 | 0 | 58 | 58 | Yes, County | No | Wailuku-Kahului |  | 2204 | 26100
M-3 | Waihee-Waikapu | Maui | 0 | 79 | 0 | 79 | Yes, County | No | Wailuku-Kahului |  | 3002 | 35550
M-4 | Kahoma | Maui | 212 | 0 | 0 | 212 | Yes, County | Yes | Lahaina WWTP |  | 8056 | 95400
M-5 | North Wailuku | Maui | 0 | 7 | 0 | 7 | Yes, County | Yes | Wailuku-Kahului |  | 266 | 3150
M-6 | Waihee-Waikapu | Maui | 0 | 8 | 0 | 8 | Yes, County | Yes | Wailuku-Kahului |  | 304 | 3600
M-7 | Kula Makai | Maui | 0 | 616 | 0 | 616 | Yes, County & Private | Yes | Kihei WWTP | Makena Resort | 23408 | 277200
M-8 | Kula | Maui | 0 | 0 | 176 | 176 | No |  |  |  | 6688 | 79200
M-9 | Kula | Maui | 0 | 0 | 209 | 209 | No |  |  |  | 7942 | 94050
Mo-1 | East Molokai | Molokai | 281 | 0 | 0 | 281 | Yes, County | No | Kaunakakai Wastewater Treatment Plant |  | 10678 | 126450
Mo-2 | West Molokai | Molokai | 0 | 0 | 100 | 100 | Yes, Private | No | Molokai Ranch WWTP |  | 3800 | 45000
O-1 | Waimanalo Bay Beach Park | Oahu | 181 | 0 | 0 | 181 | Yes, County | Yes | Waimanalo Wastewater Treatment Plant |  | 6878 | 81450
O-10 | Waianae Kai | Oahu | 86 | 102 | 0 | 188 | Yes, County | No | Waianae WWTP |  | 7144 | 84600
O-11 | Keanui Drive-Hoomahana Street | Oahu | 886 | 0 | 0 | 886 | Yes, County | Yes | Honouliuli WWTP |  | 33668 | 398700
O-12 | Kaimuki: Kapiolani Community College | Oahu | 0 | 0 | 58 | 58 | Yes, County | Yes | Sand Island WWTP/Synagro |  | 2204 | 26100
O-13 | Kapiolani Park | Oahu | 25 | 0 | 0 | 25 | Yes, County | Yes | Sand Island WWTP/Synagro |  | 950 | 11250
O-14 | Diamond Head | Oahu | 0 | 139 | 0 | 139 | Yes, County | Yes | Sand Island WWTP/Synagro |  | 5282 | 62550
O-15 | Judd Hillside-Lowrey Avenue | Oahu | 74 | 119 | 0 | 193 | Yes, County | Yes | Sand Island WWTP/Synagro |  | 7334 | 86850
O-16 | Aiea Heights | Oahu | 0 | 102 | 0 | 102 | Yes, County | Yes | Sand Island WWTP/Synagro |  | 3876 | 45900
O-17 | Ahuimanu | Oahu | 0 | 0 | 20 | 20 | Yes, County | Yes | Kailua |  | 760 | 9000
O-18 | Kaaawa | Oahu | 144 | 0 | 0 | 144 | No |  |  |  | 5472 | 64800
O-19 | Hauula | Oahu | 63 | 0 | 0 | 63 | No |  |  |  | 2394 | 28350
O-2 | Kalaheo Avenue | Oahu | 127 | 0 | 0 | 127 | Yes, County | Yes | Kailua |  | 4826 | 57150
O-20 | Sunset Beach | Oahu | 425 | 0 | 0 | 425 | No |  |  |  | 16150 | 191250
O-21 | Kawailoa | Oahu | 70 | 0 | 0 | 70 | No |  |  |  | 2660 | 31500
O-22 | Lualualei-Camp Waianae | Oahu | 0 | 99 | 0 | 99 | Yes, County | No | Waianae WWTP |  | 3762 | 44550
O-3 | Kahaluu-Waikane | Oahu | 0 | 101 | 31 | 132 | Yes, County | Yes | Kailua |  | 5016 | 59400
O-4 | Kahaluu-Waikane | Oahu | 0 | 224 | 0 | 224 | Yes, County | Yes | Kailua |  | 8512 | 100800
O-5 | Laie | Oahu | 360 | 0 | 0 | 360 | Yes, Private | Unknown | Laie WWTP (BYU-Hawaii) |  | 13680 | 162000
O-6 | Haleiwa | Oahu | 181 | 0 | 0 | 181 | Yes, County | No | Paalaa Kai WWTP |  | 6878 | 81450
O-7 | Waialua District Park | Oahu | 335 | 0 | 0 | 335 | Yes, County | No | Paalaa Kai WWTP |  | 12730 | 150750
O-8 | Mokuleia | Oahu | 396 | 0 | 0 | 396 | Yes, County | No | Paalaa Kai WWTP |  | 15048 | 178200
O-9 | Makua Valley | Oahu | 77 | 0 | 0 | 77 | Yes, County | No | Waianae WWTP |  | 2926 | 34650
M-16 | Waihee-Waikapu | Maui | 0 | 36 | 0 | 36 | Yes, County | No | Wailuku-Kahului |  | 1368 | 16200

## Costs
UID | Name | Cost_symbol | Connections | Collection_Length_ft | Conveyance_Length_ft | New_WWTP_Needed | WWTP_Upgrade_Needed | Neighborhood_Pump_Stations | Regional_Pump_Stations | Mean_slope_pct | Basalt_fraction | Terrain_Factor | Substrate_Factor | Collection_Cost | Conveyance_Cost | Treatment_Cost | Neighborhood_Pump_Cost | Regional_Pump_Cost | Planning_Cost | Cost_per_Connection | MRC: Median Relative Cost (dimensionless) | Validation category
H-1 | Pahala | (4) - $$$$ | 58 | 10710.6829 | 222 | Y | N | 0 | 0 | 7.53 | 0.6476 | 1 | 1.1295 | 23011347.92 | 827863.2892 | 8520952.138 | 0 | 0 | 32360163.34 | 557933.8507 | 1.4067 | 3
H-10 | Wainaku | (3) - $$$ | 166 | 9197.9095 | 2232 | N | N | 4 | 2 | 13.66 | 0.0983 | 1.1 | 1.0197 | 19623125.04 | 8265211.727 | 0 | 3000000 | 13066666.67 | 43955003.43 | 264789.1773 | 0.66758 | 2
H-11 | Kaūmana | (4) - $$$$ | 305 | 31372.1408 | 5280 | N | N | 6 | 2 | 4.86 | 0.7888 | 1 | 1.1578 | 69086575.65 | 20181999.37 | 0 | 4500000 | 13066666.67 | 106835241.7 | 350279.481 | 0.88312 | 2
H-12 | West Hilo | (3) - $$$ | 1919 | 150478.9296 | 108 | N | N | 29 | 10 | 6.86 | 0.899 | 1 | 1.1798 | 337687554.7 | 420672.2577 | 0 | 21750000 | 65333333.33 | 425191560.3 | 221569.3383 | 0.55862 | 4
H-13 | Hilo | (3) - $$$ | 198 | 15092.0541 | 1046 | N | N | 3 | 1 | 6.82 | 1 | 1 | 1.2 | 34447726.83 | 4144046.84 | 0 | 2250000 | 6533333.333 | 47375107.01 | 239268.2172 | 0.60324 | 2
H-14 | South Hilo | (3) - $$$ | 5206 | 421364.2409 | 1941 | N | N | 64 | 23 | 3.85 | 1 | 1 | 1.2 | 961767046.4 | 7689861.297 | 0 | 48000000 | 150266666.7 | 1167723574 | 224303.4142 | 0.56551 | 2
H-15 | Keaukaha | (3) - $$$ | 189 | 19051.2107 | 501 | N | N | 0 | 0 | 2.48 | 1 | 1 | 1.2 | 43484531.55 | 1984863.735 | 0 | 0 | 0 | 45469395.28 | 240578.811 | 0.60654 | 1
H-16 | Kuakini Heights | (3) - $$$ | 148 | 8270.3801 | 2685 | N | N | 1 | 1 | 17.62 | 1 | 1.1 | 1.2 | 20764925.09 | 11701187.71 | 0 | 750000 | 6533333.333 | 39749446.13 | 268577.3387 | 0.67713 | 2
H-17 | Holualoa | (3) - $$$ | 1549 | 105383.701 | 461 | N | N | 19 | 7 | 13.39 | 1 | 1.1 | 1.2 | 264592998.5 | 2009030.739 | 0 | 14250000 | 45733333.33 | 326585362.5 | 210836.2573 | 0.53156 | 2
H-18 | Hawaiian Beaches | (4) - $$$$ | 1152 | 207531.9237 | 5280 | Y | N | 18 | 6 | 3.26 | 0.9969 | 1 | 1.1994 | 473448434 | 20907516.59 | 83808717.5 | 13500000 | 39200000 | 630864668.1 | 547625.5799 | 1.3807 | 4
H-19 | Nanawele Estates | (5) - $$$$$ | 213 | 46664.9428 | 5280 | Y | N | 5 | 2 | 4.68 | 1 | 1 | 1.2 | 106513082.7 | 20918324.39 | 31292462.16 | 3750000 | 13066666.67 | 175540535.9 | 824133.9713 | 2.0778 | 4
H-2 | Naalehu | (5) - $$$$$ | 46 | 10049.7128 | 215 | Y | N | 0 | 1 | 7.13 | 0.0582 | 1 | 1.0116 | 19337958.03 | 718085.5339 | 6757996.523 | 0 | 6533333.333 | 33347373.42 | 724942.9005 | 1.8277 | 4
H-20 | Seaview | (5) - $$$$$ | 187 | 39802.58 | 5280 | Y | N | 4 | 1 | 3.48 | 1 | 1 | 1.2 | 90849687.99 | 20918324.39 | 27472725 | 3000000 | 6533333.333 | 148774070.7 | 795583.2659 | 2.0058 | 4
H-21 | Kehena | (5) - $$$$$ | 44 | 9795.1163 | 5280 | Y | N | 2 | 1 | 7.81 | 0.9992 | 1 | 1.1998 | 22354445.65 | 20915535.28 | 6464170.588 | 1500000 | 6533333.333 | 57767484.85 | 1312897.383 | 3.3101 | 4
H-22 | Kaʻohe | (5) - $$$$$ | 120 | 9502.7232 | 5280 | Y | N | 3 | 1 | 27.09 | 1 | 1.1 | 1.2 | 23859040.8 | 23010156.83 | 17629556.15 | 2250000 | 6533333.333 | 73282087.12 | 610684.0593 | 1.5396 | 4
H-23 | Kīloa | (4) - $$$$ | 187 | 13700.7487 | 5280 | Y | N | 2 | 1 | 15.22 | 1 | 1.1 | 1.2 | 34399267.96 | 23010156.83 | 27472725 | 1500000 | 6533333.333 | 92915483.12 | 496874.2413 | 1.2527 | 4
H-24 | Captain Cook | (5) - $$$$$ | 110 | 9759.5198 | 5280 | Y | N | 2 | 1 | 14.53 | 1 | 1.1 | 1.2 | 24503794.96 | 23010156.83 | 16160426.47 | 1500000 | 6533333.333 | 71707711.59 | 651888.2872 | 1.6435 | 4
H-25 | Kealakekua | (4) - $$$$ | 314 | 26330.6457 | 8536 | N | Y | 5 | 2 | 13.6 | 1 | 1.1 | 1.2 | 66109886.26 | 37199753.55 | 46130671.92 | 3750000 | 13066666.67 | 166256978.4 | 529480.8229 | 1.3349 | 4
H-26 | Kalaoa | (4) - $$$$ | 1616 | 171497.5017 | 5280 | Y | N | 39 | 14 | 11.27 | 1 | 1.1 | 1.2 | 430588770.1 | 23010156.83 | 117565006.5 | 29250000 | 91466666.67 | 691880600.1 | 428143.9357 | 1.0794 | 4
H-27 | Haiwi | (4) - $$$$ | 331 | 27535.644 | 5280 | Y | N | 6 | 2 | 7.8 | 1 | 1 | 1.2 | 62850314.36 | 20918324.39 | 48628192.37 | 4500000 | 13066666.67 | 149963497.8 | 453061.9269 | 1.1423 | 4
H-28 | Kapaau | (5) - $$$$$ | 222 | 17702.8821 | 5280 | Y | N | 7 | 3 | 10.62 | 1 | 1.1 | 1.2 | 44447657.47 | 23010156.83 | 32614678.87 | 5250000 | 19600000 | 124922493.2 | 562713.9332 | 1.4187 | 4
H-29 | Puʻukapu Homesteads | (4) - $$$$ | 181 | 12402.537 | 5280 | Y | N | 1 | 1 | 4.55 | 1 | 1 | 1.2 | 28308883.95 | 20918324.39 | 26591247.19 | 750000 | 6533333.333 | 83101788.87 | 459125.9054 | 1.1575 | 4
H-3 | Hillcrest | (3) - $$$ | 88 | 4238.0781 | 354 | N | N | 2 | 1 | 10.52 | 1 | 1.1 | 1.2 | 10640789.64 | 1542726.424 | 0 | 1500000 | 6533333.333 | 20216849.4 | 229736.925 | 0.57921 | 4
H-30 | Puʻukapu Homesteads East | (4) - $$$$ | 244 | 11485.857 | 5280 | Y | N | 1 | 0 | 3.58 | 1 | 1 | 1.2 | 26216554.83 | 20918324.39 | 35846764.17 | 750000 | 0 | 83731643.39 | 343162.4729 | 0.86518 | 4
H-31 | Ola Mamalahoa Hwy West | (4) - $$$$ | 253 | 14755.9158 | 5280 | Y | N | 2 | 1 | 5.35 | 1 | 1 | 1.2 | 33680488.59 | 20918324.39 | 37168980.88 | 1500000 | 6533333.333 | 99801127.2 | 394470.8585 | 0.99453 | 4
H-32 | Paauilo | (5) - $$$$$ | 139 | 12082.9402 | 5280 | Y | N | 3 | 1 | 17.68 | 1 | 1.1 | 1.2 | 30337341.89 | 23010156.83 | 20420902.54 | 2250000 | 6533333.333 | 82551734.59 | 593897.3712 | 1.4973 | 4
H-33 | Laupahoehoe | (4) - $$$$ | 129 | 11623.5808 | 5280 | Y | N | 1 | 0 | 15.5 | 1 | 1.1 | 1.2 | 29184001.53 | 23010156.83 | 18951772.86 | 750000 | 0 | 71895931.22 | 557332.8002 | 1.4051 | 4
H-34 | Ponahawai | (5) - $$$$$ | 129 | 18542.2261 | 5280 | Y | N | 0 | 0 | 9.07 | 1 | 1 | 1.2 | 42322770.37 | 20918324.39 | 18951772.86 | 0 | 0 | 82192867.63 | 637154.0126 | 1.6064 | 4
H-35 | Kaūmana Homesteads | (4) - $$$$ | 125 | 9422.6305 | 5280 | Y | N | 1 | 0 | 5.84 | 0.9884 | 1 | 1.1977 | 21465644.21 | 20877882.3 | 18364120.99 | 750000 | 0 | 61457647.5 | 491661.18 | 1.2396 | 4
H-36 | Keaau | (5) - $$$$$ | 188 | 26054.3607 | 5280 | Y | N | 6 | 2 | 4.76 | 1 | 1 | 1.2 | 59469274.05 | 20918324.39 | 27619637.96 | 4500000 | 13066666.67 | 125573903.1 | 667946.293 | 1.684 | 4
H-37 | Mountain View | (5) - $$$$$ | 109 | 16259.4049 | 5280 | Y | N | 0 | 0 | 6.16 | 1 | 1 | 1.2 | 37112213.92 | 20918324.39 | 16013513.5 | 0 | 0 | 74044051.81 | 679303.2277 | 1.7127 | 4
H-38 | Tiki Gardens | (5) - $$$$$ | 624 | 130434.6908 | 5280 | Y | N | 6 | 2 | 3.45 | 1 | 1 | 1.2 | 297718162 | 20918324.39 | 91673691.97 | 4500000 | 13066666.67 | 427876845 | 685700.0721 | 1.7288 | 4
H-39 | Waiʻaka | (5) - $$$$$ | 283 | 25633.3587 | 11216 | N | Y | 5 | 2 | 7.35 | 1 | 1 | 1.2 | 58508333.94 | 44435592.12 | 41576369.92 | 3750000 | 13066666.67 | 161336962.6 | 570095.2743 | 1.4373 | 4
H-4 | Kailua-Kona | (3) - $$$ | 680 | 46709.2067 | 3783 | N | N | 13 | 5 | 9.93 | 1 | 1 | 1.2 | 106614115.2 | 14987504.01 | 0 | 9750000 | 32666666.67 | 164018285.9 | 241203.3617 | 0.60812 | 2
H-40 | Waimea | (4) - $$$$ | 585 | 69377.458 | 10 | N | Y | 9 | 3 | 6.91 | 0.8728 | 1 | 1.1746 | 154997452.4 | 38778.1362 | 85944086.22 | 6750000 | 19600000 | 267330316.8 | 456974.9005 | 1.1521 | 4
H-41 | East Waimea | (5) - $$$$$ | 225 | 28577.996 | 6343 | N | Y | 4 | 2 | 10.47 | 1 | 1.1 | 1.2 | 71752439.65 | 27642694.09 | 33055417.78 | 3000000 | 13066666.67 | 148517218.2 | 660076.5253 | 1.6642 | 4
H-42 | Puako | (4) - $$$$ | 120 | 9897.9787 | 6165 | N | Y | 0 | 0 | 2.04 | 0.8985 | 1 | 1.1797 | 22210025.82 | 24011339.33 | 17629556.15 | 0 | 0 | 63850921.3 | 532091.0108 | 1.3415 | 4
H-5 | Kealakehe HHL | (2) - $$ | 503 | 28340.677 | 32 | N | N | 7 | 3 | 10.62 | 1 | 1.1 | 1.2 | 71156588.96 | 139455.496 | 0 | 5250000 | 19600000 | 96146044.45 | 191145.2176 | 0.48191 | 4
H-6 | Honokaa | (4) - $$$$ | 631 | 64566.7207 | 15 | N | Y | 13 | 5 | 12.04 | 1 | 1.1 | 1.2 | 162111427.7 | 65369.7637 | 92702082.74 | 9750000 | 32666666.67 | 297295546.9 | 471149.8366 | 1.1879 | 4
H-7 | Paauhau | (5) - $$$$$ | 115 | 8387.2117 | 11602 | N | N | 1 | 1 | 13.65 | 1 | 1.1 | 1.2 | 21058261.22 | 50561333.25 | 0 | 750000 | 6533333.333 | 78902927.8 | 686112.4157 | 1.7298 | 2
H-8 | Honomu | (4) - $$$$ | 202 | 13707.9341 | 16335 | N | N | 1 | 1 | 15.72 | 1 | 1.1 | 1.2 | 34417308.91 | 71187672.7 | 0 | 750000 | 6533333.333 | 112888314.9 | 558853.0443 | 1.409 | 2
H-9 | Wainaku West | (3) - $$$ | 170 | 10628.8035 | 5731 | N | N | 0 | 0 | 13.24 | 0.0678 | 1.1 | 1.0136 | 22540186.08 | 21095230.81 | 0 | 0 | 0 | 43635416.89 | 256678.9229 | 0.64714 | 2
K-1 | Kekaha | (4) - $$$$ | 890 | 69325.7962 | 4507 | N | Y | 2 | 1 | 1.28 | 0 | 1 | 1 | 131863875.8 | 14879875.01 | 130752541.4 | 1500000 | 6533333.333 | 285529625.5 | 320819.804 | 0.80885 | 4
K-10 | Puhi | (3) - $$$ | 257 | 15037.1823 | 31 | N | Y | 3 | 1 | 3.64 | 0.999 | 1 | 1.1998 | 34316761.19 | 122795.4504 | 37756632.75 | 2250000 | 6533333.333 | 80979522.73 | 315095.4192 | 0.79441 | 4
K-11 | Haena | (4) - $$$$ | 122 | 10421.0583 | 5280 | Y | N | 0 | 0 | 2.13 | 0 | 1 | 1 | 19821786.49 | 17431936.99 | 17923382.08 | 0 | 0 | 55177105.57 | 452271.3572 | 1.1403 | 4
K-12 | Kilauea | (4) - $$$$ | 572 | 37704.2982 | 5280 | Y | N | 10 | 4 | 11.06 | 1 | 1.1 | 1.2 | 94666378.37 | 23010156.83 | 84034217.64 | 7500000 | 26133333.33 | 235344086.2 | 411440.7101 | 1.0373 | 4
K-13 | Kipuka St | (3) - $$$ | 77 | 4300.4516 | 1697 | N | N | 1 | 0 | 4.49 | 1 | 1 | 1.2 | 9815813.187 | 6723181.154 | 0 | 750000 | 0 | 17288994.34 | 224532.394 | 0.56609 | 2
K-14 | Hoona Rd | (3) - $$$ | 64 | 4118.1488 | 1907 | N | N | 0 | 0 | 6.43 | 0.9649 | 1 | 1.193 | 9344717.386 | 7510962.28 | 0 | 0 | 0 | 16855679.67 | 263369.9948 | 0.664 | 2
K-15 | Koloa | (3) - $$$ | 348 | 30337.7942 | 402 | N | N | 3 | 1 | 3.08 | 0.9982 | 1 | 1.1996 | 69225469.31 | 1592167.359 | 0 | 2250000 | 6533333.333 | 79600970 | 228738.4196 | 0.57669 | 4
K-16 | Omao | (4) - $$$$ | 231 | 13932.4395 | 13997 | N | N | 4 | 2 | 12.37 | 0.8549 | 1.1 | 1.171 | 34135030.81 | 59523553.5 | 0 | 3000000 | 13066666.67 | 109725251 | 475001.0865 | 1.1976 | 2
K-17 | Lawai | (4) - $$$$ | 520 | 45021.0449 | 16928 | N | N | 11 | 4 | 15.6 | 0.7138 | 1.1 | 1.1428 | 107645097.6 | 70253034.99 | 0 | 8250000 | 26133333.33 | 212281465.9 | 408233.5883 | 1.0292 | 2
K-18 | Anahola | (5) - $$$$$ | 201 | 24848.5832 | 5280 | Y | N | 3 | 1 | 5.89 | 0.9999 | 1 | 1.2 | 56716132.72 | 20917975.75 | 29529506.55 | 2250000 | 6533333.333 | 115946948.4 | 576850.4893 | 1.4543 | 4
K-19 | Kalaheo | (4) - $$$$ | 1325 | 91850.2968 | 5280 | Y | N | 29 | 10 | 14.31 | 0.8821 | 1.1 | 1.1764 | 226082328.9 | 22558007.25 | 96394575.25 | 21750000 | 65333333.33 | 432118244.7 | 326126.9772 | 0.82223 | 4
K-2 | Kapaa/Kawaihau | (3) - $$$ | 1793 | 102631.3409 | 5 | N | Y | 25 | 9 | 11.16 | 0.9286 | 1.1 | 1.1857 | 254616066 | 21530.6212 | 130441866.7 | 18750000 | 58800000 | 462629463.3 | 258019.7788 | 0.65052 | 4
K-20 | Hanalei | (4) - $$$$ | 204 | 17625.3433 | 14181 | N | Y | 1 | 0 | 1.78 | 0 | 1 | 1 | 33524982.1 | 46818617.14 | 29970245.45 | 750000 | 0 | 111063844.7 | 544430.6112 | 1.3726 | 4
K-21 | Hanapepe | (1) - $ | 339 | 10287.4455 | 91 | N | N | 1 | 0 | 12.36 | 0.8967 | 1.1 | 1.1793 | 25384594.48 | 389748.8401 | 0 | 750000 | 0 | 26524343.32 | 78242.9006 | 0.19726 | 4
K-3 | Apopo Rd | (4) - $$$$ | 55 | 4813.3995 | 510 | N | N | 1 | 1 | 14.04 | 0.6079 | 1.1 | 1.1216 | 11295509.35 | 2077326.889 | 0 | 750000 | 6533333.333 | 20656169.57 | 375566.7194 | 0.94687 | 2
K-4 | Kapaa | (3) - $$$ | 237 | 25390.0566 | 122 | N | N | 0 | 1 | 1.66 | 0 | 1 | 1 | 48294162.56 | 402783.3927 | 0 | 0 | 6533333.333 | 55230279.28 | 233039.1531 | 0.58754 | 4
K-5 | Wailua | (2) - $$ | 652 | 37298.9853 | 347 | N | N | 8 | 3 | 5.43 | 0.7604 | 1 | 1.1521 | 81735481.28 | 1319847.752 | 0 | 6000000 | 19600000 | 108655329 | 166649.2777 | 0.42015 | 4
K-6 | Olohena | (4) - $$$$ | 185 | 11458.5852 | 16732 | N | N | 2 | 1 | 5.72 | 0.3442 | 1 | 1.0688 | 23295641.07 | 59043525.21 | 0 | 1500000 | 6533333.333 | 90372499.62 | 488499.9979 | 1.2316 | 2
K-7 | Wailua Homesteads | (4) - $$$$ | 909 | 56169.6832 | 10378 | N | Y | 17 | 6 | 17.73 | 0.9675 | 1.1 | 1.1935 | 140264592.1 | 44982180.08 | 133543887.8 | 12750000 | 39200000 | 370740660 | 407855.5115 | 1.0283 | 4
K-8 | Lihue | (4) - $$$$ | 70 | 5008.5801 | 258 | N | Y | 1 | 1 | 13.4 | 0.965 | 1.1 | 1.193 | 12501977.71 | 1117801.17 | 10283907.75 | 750000 | 6533333.333 | 31187019.96 | 445528.8566 | 1.1233 | 4
K-9 | Pua Loke, Ulu Mahi, Ulu Ko | (4) - $$$$ | 348 | 19579.5012 | 88 | N | Y | 6 | 2 | 10.88 | 0.7478 | 1.1 | 1.1496 | 47093061.21 | 367382.7207 | 51125712.83 | 4500000 | 13066666.67 | 116152823.4 | 333772.4811 | 0.8415 | 4
M-1 | Waikapu | (3) - $$$ | 125 | 9629.5953 | 45 | N | Y | 0 | 0 | 7.58 | 0 | 1 | 1 | 18316352.97 | 148567.6448 | 18364120.99 | 0 | 0 | 36829041.61 | 294632.3328 | 0.74282 | 3
M-10 | Haiku | (4) - $$$$ | 253 | 21694.8515 | 5280 | Y | N | 1 | 1 | 15.07 | 1 | 1.1 | 1.2 | 54470527.7 | 23010156.83 | 37168980.88 | 750000 | 6533333.333 | 121932998.7 | 481948.6116 | 1.2151 | 4
M-11 | East Haiku | (5) - $$$$$ | 99 | 7152.2563 | 5280 | Y | N | 3 | 1 | 18.42 | 1 | 1.1 | 1.2 | 17957586.72 | 23010156.83 | 14544383.82 | 2250000 | 6533333.333 | 64295460.7 | 649449.098 | 1.6374 | 4
M-12 | Hana | (5) - $$$$$ | 108 | 7461.9548 | 5280 | Y | N | 2 | 1 | 10.55 | 0.9756 | 1.1 | 1.1951 | 18658975.1 | 22916582.19 | 15866600.53 | 1500000 | 6533333.333 | 65475491.16 | 606254.5478 | 1.5285 | 4
M-13 | Paʻuwela | (5) - $$$$$ | 108 | 11557.9547 | 5280 | Y | N | 1 | 1 | 11.28 | 1 | 1.1 | 1.2 | 29019230.28 | 23010156.83 | 15866600.53 | 750000 | 6533333.333 | 75179320.98 | 696104.8239 | 1.755 | 4
M-14 | Pukalani | (4) - $$$$ | 1207 | 116827.1458 | 5280 | N | Y | 17 | 6 | 8.73 | 1 | 1 | 1.2 | 266658838.3 | 20918324.39 | 87810001.76 | 12750000 | 39200000 | 427337164.4 | 354049.0177 | 0.89262 | 4
M-15 | Makawao | (3) - $$$ | 1802 | 113354.6424 | 7872 | N | Y | 22 | 8 | 8.47 | 1 | 1 | 1.2 | 258732823.1 | 31187320 | 131096622.3 | 16500000 | 52266666.67 | 489783432.2 | 271799.9069 | 0.68526 | 4
M-2 | Old Wailuku Heights | (3) - $$$ | 58 | 3379.6431 | 405 | N | Y | 0 | 0 | 17.48 | 0.1729 | 1.1 | 1.0346 | 7315745.164 | 1521680.629 | 8520952.138 | 0 | 0 | 17358377.93 | 299282.3781 | 0.75455 | 3
M-3 | Waihee | (3) - $$$ | 79 | 4088.5759 | 903 | N | Y | 1 | 0 | 7.01 | 0 | 1 | 1 | 7776837.655 | 2981257.406 | 11606124.46 | 750000 | 0 | 23114219.53 | 292585.0573 | 0.73766 | 4
M-4 | Wahikuli | (1) - $ | 212 | 10316.043 | 90 | N | N | 0 | 0 | 6.9 | 1 | 1 | 1.2 | 23546445.59 | 356562.3476 | 0 | 0 | 0 | 23903007.94 | 112750.0375 | 0.28426 | 1
M-5 | Pakele Place | (4) - $$$$ | 7 | 472.844 | 250 | N | N | 1 | 0 | 3.19 | 0 | 1 | 1 | 899391.7354 | 825375.8046 | 0 | 750000 | 0 | 2474767.54 | 353538.22 | 0.89134 | 4
M-6 | Waikapu-North | (3) - $$$ | 8 | 856.6245 | 169 | N | N | 0 | 0 | 6.94 | 0 | 1 | 1 | 1629376.62 | 557954.0439 | 0 | 0 | 0 | 2187330.664 | 273416.333 | 0.68933 | 1
M-7 | Maui Meadows | (3) - $$$ | 616 | 43613.3601 | 1575 | N | N | 9 | 3 | 10.5 | 1 | 1.1 | 1.2 | 109502604.4 | 6863825.191 | 0 | 6750000 | 19600000 | 142716429.6 | 231682.5155 | 0.58411 | 2
M-8 | Kula | (5) - $$$$$ | 176 | 25500.7781 | 5280 | Y | N | 5 | 2 | 18.49 | 1 | 1.1 | 1.2 | 64026289.32 | 23010156.83 | 25856682.35 | 3750000 | 13066666.67 | 129709795.2 | 736987.4725 | 1.8581 | 4
M-9 | ʻŌmaʻopio | (4) - $$$$ | 209 | 17844.5812 | 5280 | Y | N | 3 | 1 | 13.6 | 1 | 1.1 | 1.2 | 44803429.76 | 23010156.83 | 30704810.29 | 2250000 | 6533333.333 | 107301730.2 | 513405.4077 | 1.2944 | 4
Mo-1 | Puili and Pano Pl | (4) - $$$$ | 281 | 23812.4202 | 4078 | N | Y | 1 | 0 | 8.51 | 0.5435 | 1 | 1.1087 | 50216744.61 | 14927015.85 | 41282543.98 | 750000 | 0 | 107176304.4 | 381410.3361 | 0.96161 | 4
Mo-2 | North Kalae Hwy | (5) - $$$$$ | 100 | 5848.9641 | 13509 | N | Y | 3 | 1 | 11.72 | 0.9153 | 1.1 | 1.1831 | 14478026.91 | 58040932.68 | 14691296.79 | 2250000 | 6533333.333 | 95993589.72 | 959935.8972 | 2.4202 | 4
O-1 | Waimanalo Beach | (2) - $$ | 181 | 11985.1993 | 18 | N | N | 0 | 0 | 4.23 | 0 | 1 | 1 | 22796922.86 | 59427.0579 | 0 | 0 | 0 | 22856349.91 | 126278.1763 | 0.31837 | 1
O-10 | Waianae | (2) - $$ | 188 | 3269.6776 | 89 | N | Y | 1 | 0 | 7.5 | 0 | 1 | 1 | 6219219.798 | 293833.7865 | 27619637.96 | 750000 | 0 | 34882691.55 | 185546.2316 | 0.4678 | 4
O-11 | Ewa Beach | (1) - $ | 886 | 34500.6368 | 25 | N | N | 2 | 1 | 1.75 | 0 | 1 | 1 | 65623302.23 | 82537.5805 | 0 | 1500000 | 6533333.333 | 73739173.15 | 83227.0577 | 0.20983 | 4
O-12 | Kaimuki | (1) - $ | 58 | 1883.6573 | 79 | N | N | 1 | 0 | 10.38 | 0.0058 | 1.1 | 1.0012 | 3945745.123 | 287233.4344 | 0 | 750000 | 0 | 4982978.558 | 85913.4234 | 0.2166 | 4
O-13 | Diamond head - West | (4) - $$$$ | 25 | 3593.0923 | 226 | N | N | 2 | 0 | 29.36 | 0 | 1.1 | 1 | 7517821.735 | 820753.7001 | 0 | 1500000 | 0 | 9838575.435 | 393543.0174 | 0.9922 | 4
O-14 | Diamond head - East | (3) - $$$ | 139 | 9951.6063 | 131 | N | N | 6 | 2 | 10.82 | 0.2674 | 1.1 | 1.0535 | 21935277.6 | 501189.5427 | 0 | 4500000 | 13066666.67 | 40003133.81 | 287792.3296 | 0.72558 | 4
O-15 | Tantalus | (4) - $$$$ | 193 | 28345.0024 | 154 | N | N | 1 | 1 | 27.62 | 0.1715 | 1.1 | 1.0343 | 61340410.54 | 578457.7656 | 0 | 750000 | 6533333.333 | 69202201.64 | 358560.6303 | 0.904 | 4
O-16 | Aiea Heights | (3) - $$$ | 102 | 6562.0389 | 1253 | N | N | 3 | 1 | 21.15 | 1 | 1.1 | 1.2 | 16475693.38 | 5460554.263 | 0 | 2250000 | 6533333.333 | 30719580.98 | 301172.3625 | 0.75931 | 2
O-17 | Kahaluu - Kamehameha HWY | (2) - $$ | 20 | 1454.8837 | 6 | N | N | 0 | 0 | 20.24 | 0.9203 | 1.1 | 1.1841 | 3604339.172 | 25800.5742 | 0 | 0 | 0 | 3630139.746 | 181506.9873 | 0.45761 | 1
O-18 | Kaaawa | (5) - $$$$$ | 144 | 20731.0172 | 5280 | Y | N | 0 | 0 | 13.35 | 0.0463 | 1.1 | 1.0093 | 43777134.3 | 19352692.4 | 21155467.38 | 0 | 0 | 84285294.08 | 585314.5423 | 1.4757 | 4
O-19 | Hauula | (4) - $$$$ | 63 | 3214.4401 | 5280 | Y | N | 0 | 0 | 1.98 | 0 | 1 | 1 | 6114153.058 | 17431936.99 | 9255516.978 | 0 | 0 | 32801607.03 | 520660.429 | 1.3127 | 4
O-2 | Kailua | (2) - $$ | 127 | 9906.3601 | 1059 | N | N | 0 | 0 | 2.22 | 0 | 1 | 1 | 18842784.57 | 3496291.908 | 0 | 0 | 0 | 22339076.47 | 175898.2399 | 0.44347 | 2
O-20 | Pupukea | (4) - $$$$ | 425 | 49514.355 | 5280 | Y | N | 8 | 3 | 14.35 | 0.188 | 1.1 | 1.0376 | 107494128.8 | 19896115.61 | 62438011.36 | 6000000 | 19600000 | 215428255.8 | 506890.0136 | 1.278 | 4
O-21 | Kawailoa | (4) - $$$$ | 70 | 3253.406 | 5280 | Y | N | 1 | 0 | 4.63 | 0.1216 | 1 | 1.0243 | 6338768.466 | 17855881.7 | 10283907.75 | 750000 | 0 | 35228557.92 | 503265.1132 | 1.2688 | 4
O-22 | Waianae Hawaiian Homeland | (4) - $$$$ | 99 | 11771.5013 | 6 | N | Y | 1 | 0 | 8.01 | 0 | 1 | 1 | 22390450.11 | 19809.0193 | 14544383.82 | 750000 | 0 | 37704642.95 | 380854.9793 | 0.96021 | 4
O-3 | Ahuimanu | (3) - $$$ | 132 | 12671.3052 | 112 | N | N | 2 | 1 | 25.27 | 0 | 1.1 | 1 | 26512153.65 | 406745.1965 | 0 | 1500000 | 6533333.333 | 34952232.18 | 264789.6377 | 0.66758 | 4
O-4 | Kahaluu | (3) - $$$ | 224 | 23830.0341 | 1493 | N | N | 5 | 2 | 6.47 | 0 | 1 | 1 | 45326859.89 | 4929144.305 | 0 | 3750000 | 13066666.67 | 67072670.87 | 299431.5664 | 0.75492 | 2
O-5 | North Hauula | (4) - $$$$ | 360 | 30580.5034 | 9713 | N | Y | 2 | 1 | 6.08 | 0.0066 | 1 | 1.0013 | 58243637.64 | 32109829.86 | 52888668.44 | 1500000 | 6533333.333 | 151275469.3 | 420209.6369 | 1.0594 | 4
O-6 | Waialua and Haleiwa | (4) - $$$$ | 181 | 12876.7653 | 6045 | N | Y | 1 | 0 | 1.56 | 0 | 1 | 1 | 24492761.4 | 19957586.96 | 26591247.19 | 750000 | 0 | 71791595.55 | 396638.6494 | 1 | 4
O-7 | Waialua | (4) - $$$$ | 335 | 39004.5738 | 7661 | N | Y | 3 | 1 | 3.83 | 0 | 1 | 1 | 74190193.98 | 25292816.16 | 49215844.25 | 2250000 | 6533333.333 | 157482187.7 | 470096.0827 | 1.1852 | 4
O-8 | Mokuleia | (4) - $$$$ | 396 | 33560.2474 | 6050 | N | Y | 0 | 0 | 1.5 | 0 | 1 | 1 | 63834597.38 | 19974094.47 | 58177535.29 | 0 | 0 | 141986227.1 | 358551.0786 | 0.90397 | 4
O-9 | Makaha | (4) - $$$$ | 77 | 6905.0462 | 2404 | N | Y | 0 | 0 | 3.17 | 0 | 1 | 1 | 13134016.5 | 7936813.737 | 11312298.53 | 0 | 0 | 32383128.77 | 420560.1139 | 1.0603 | 4
M-16 | Waikapu-South | (2) - $$ | 36 | 2406.2303 | 45 | N | N | 0 | 0 | 7.58 | 0 | 1 | 1 | 4576865.632 | 148567.6448 | 0 | 0 | 0 | 4725433.277 | 131262.0355 | 0.33094 | 1

## CostModel_Parameters
Parameter | Cost
Collection cost per linear foot | 1902.0896
Conveyance / force main cost per linear foot | 3301.5032
Neighborhood pump station (street-scale) — cost each | 750000
Regional pump station — cost each | 6533333.333
TERRAIN AND SUBSTRATE MULTIPLIERS | Default Value
Terrain factor (steep slopes) | 1.1
Substrate factor (hard rock / lava / basalt) | 1.2
WW TREATMENT PLANT COST — three size tiers
Small / decentralized treatment (≤ 1,000 connections) | 146912.9679
Medium / regional treatment (1,001 – 10,000 connections) | 72750.6228
Large / centralized treatment (> 10,000 connections) | 18667.9815
COST RATING THRESHOLDS (cost per connection) | Upper Bound ($/conn) | Tier | Meaning
Below this → rated $ | 120000 | (1) - $ | Lowest relative cost
Below this → rated $$ | 200000 | (2) - $$ | Low to Medium relative cost
Below this → rated $$$ | 320000 | (3) - $$$ | Moderate relative cost
Below this → rated $$$$ | 560000 | (4) - $$$$ | High relative cost
At or above → rated $$$$$ |  | (5) - $$$$$ | Highest relative cost

## CostModel_Data
Project_Name | Island | Source_Org | Dollar_Year | Component_Group | Component_Type | Quantity | Quantity_Unit | Total_Cost | Connections | Unit_Cost | Citation | Notes | Cost_Basis | Complicating_Factor_Collection | Complicating_Factor_Conveyance | Factor_Note | Document URL
Kiahuna Golf Course | Kauai | Carollo | 2026 | Collection | Gravity Main | 5300 | LF | 15105000 |  | 2850 | Carollo Draft 2026 EPA Grant County Studies | Gravity collection (5,300 LF; actual blended $/LF = $2,850/LF vs Carollo baseline $2,850. 100% gravity; connects to Poipu WRF; minimal additional costs ($95K) | Component_Known | None | None | Note: Where Carollo reported total piping costs alongside gravity and low-pressure sewer proportions, the total piping cost was allocated between components in proportion to the reported shares. component-level costs were used where the studies reported separable collection, conveyance, or treatment costs
Kipuka St | Kauai | Carollo | 2026 | Collection | Gravity Main | 3900 | LF | 11115000 |  | 2850 | Carollo Draft 2026 EPA Grant County Studies | Collection only (3,900 LF of 8 in. gravity); cost derived at Carollo $2,850/LF baseline rate; project also includes 4,300 LF FM + WWPS (see Project Total row). Component_Estimated because cost derived from baseline rate, not independently measured. | Component_Estimated | None | None
Puhi | Kauai | Carollo | 2026 | Collection | Gravity Main | 1580 | LF | 3507600 |  | 2220 | Carollo Draft 2026 EPA Grant County Studies | Gravity collection (1,580 LF; 10% of 15,800 total LF; pipe base cost split proportionally from Carollo Weighted Base Cost of Piping Alone ($35,076,000); actual blended $/LF = $2,220/LF vs Carollo baseline $2,850. 10% gravity / 90% LPS; multiple diameters (4, 8, 12 in.); connects to Lihue-Puhi WRF | Component_Estimated | None | None
Pukalani | Maui | Carollo | 2026 | Collection | Gravity Main | 36666 | LF | 89611704 |  | 2444 | Carollo Draft 2026 EPA Grant County Studies | Gravity collection (36,666 LF; 42% of 87,300 total LF; pipe base cost split proportionally from Carollo Weighted Base Cost of Piping Alone ($213,361,200); actual blended $/LF = $2,444/LF vs Carollo baseline $2,850. 42% gravity / 58% LPS; largest private project by connections; trunk line premium (12-18 in. diameters) | Component_Estimated | None | None
Waialua | Oahu | Carollo | 2026 | Collection | Gravity Main | 34496 | LF | 84791168 |  | 2458 | Carollo Draft 2026 EPA Grant County Studies | Gravity collection (34,496 LF; 44% of 78,400 total LF; pipe base cost split proportionally from Carollo Weighted Base Cost of Piping Alone ($192,707,200); actual blended $/LF = $2,458/LF vs Carollo baseline $2,850. 44% gravity / 56% LPS; anomalously high additional costs ($198.8M) - clarify with Carollo whether WWTP/receiving system upgrades included | Component_Estimated | None | None
Ewa | Oahu | Carollo | 2026 | Collection | Gravity Main | 30700 | LF | 87495000 |  | 2850 | Carollo Draft 2026 EPA Grant County Studies | Gravity collection (30,700 LF; actual blended $/LF = $2,850/LF vs Carollo baseline $2,850. 100% gravity; 8 and 12 in. pipe; additional costs $8.4M may reflect larger diameter pipe premium | Component_Known | None | None
Kahaluu | Oahu | Carollo | 2026 | Collection | Gravity Main | 15215 | LF | 39185000 |  | 2575.419 | Carollo Draft 2026 EPA Grant County Studies | Gravity collection (15,215 LF; 85% of 17,900 total LF; pipe base cost split proportionally from Carollo Weighted Base Cost of Piping Alone ($46,100,000); actual blended $/LF = $2,575/LF vs Carollo baseline $2,850. 85% gravity / 15% LPS; dispersed layout; high LF/conn ratio (108 LF/conn); actual blended $/LF ($2,575) below weighted baseline ($2,745) | Component_Estimated | None | None
Ahuimanu | Oahu | Carollo | 2026 | Collection | Gravity Main | 546 | LF | 1113000 |  | 2038.4615 | Carollo Draft 2026 EPA Grant County Studies | Gravity collection (546 LF; 7% of 7,800 total LF; pipe base cost split proportionally from Carollo Weighted Base Cost of Piping Alone ($15,900,000); actual blended $/LF = $2,038/LF vs Carollo baseline $2,850. 7% gravity / 93% LPS; actual blended $/LF ($2,038) lowest among all public extensions; below weighted baseline ($2,199) | Component_Estimated | None | None
Kailua | Oahu | Carollo | 2026 | Collection | Gravity Main | 6000 | LF | 17100000 |  | 2850 | Carollo Draft 2026 EPA Grant County Studies | Gravity collection (6,000 LF; actual blended $/LF = $2,850/LF vs Carollo baseline $2,850. 100% gravity; coastal peninsula; compact layout (35 LF/conn); modest additional costs ($1.3M) | Component_Known | None | None
Makaha | Oahu | Carollo | 2026 | Collection | Gravity Main | 2414 | LF | 5304000 |  | 2197.1831 | Carollo Draft 2026 EPA Grant County Studies | Gravity collection (2,414 LF; 34% of 7,100 total LF; pipe base cost split proportionally from Carollo Weighted Base Cost of Piping Alone ($15,600,000); actual blended $/LF = $2,197/LF vs Carollo baseline $2,850. 34% gravity / 66% LPS; linear beachfront along Farrington Hwy; actual $/LF ($2,197) below baseline ($2,388) | Component_Estimated | None | None
Kaupuni | Oahu | Carollo | 2026 | Collection | Gravity Main | 3850 | LF | 9759750 |  | 2535 | Carollo Draft 2026 EPA Grant County Studies | Gravity collection (3,850 LF; 55% of 7,000 total LF; pipe base cost split proportionally from Carollo Weighted Base Cost of Piping Alone ($17,745,000); actual blended $/LF = $2,535/LF vs Carollo baseline $2,850. 55% gravity / 45% LPS; infill project; two non-contiguous cesspool clusters in Waianae Valley | Component_Estimated | None | None
Waimanalo Beach | Oahu | Carollo | 2026 | Collection | Gravity Main | 13800 | LF | 39330000 |  | 2850 | Carollo Draft 2026 EPA Grant County Studies | Gravity collection (13,800 LF; actual blended $/LF = $2,850/LF vs Carollo baseline $2,850. 100% gravity; linear beachfront; multiple connection points along Kalanianaole Hwy | Component_Known | None | None
Kaimuki | Oahu | Carollo | 2026 | Collection | Gravity Main | 528 | LF | 1216512 |  | 2304 | Carollo Draft 2026 EPA Grant County Studies | Gravity collection (528 LF; 22% of 2,400 total LF; pipe base cost split proportionally from Carollo Weighted Base Cost of Piping Alone ($5,529,600); actual blended $/LF = $2,304/LF vs Carollo baseline $2,850. 22% gravity / 78% LPS; smallest public project; urban infill near Diamond Head crater | Component_Estimated | None | None
Makiki | Oahu | Carollo | 2026 | Collection | Gravity Main | 16000 | LF | 41760000 |  | 2610 | Carollo Draft 2026 EPA Grant County Studies | Gravity collection (16,000 LF; 80% of 20,000 total LF; pipe base cost split proportionally from Carollo Weighted Base Cost of Piping Alone ($52,200,000); actual blended $/LF = $2,610/LF vs Carollo baseline $2,850. 80% gravity / 20% LPS; hillside community Makiki Heights/Round Top; natural slope aids gravity flow | Component_Estimated | None | None
Diamond Head | Oahu | Carollo | 2026 | Collection | Gravity Main | 1173 | LF | 2661537 |  | 2269 | Carollo Draft 2026 EPA Grant County Studies | Gravity collection (1,173 LF; 17% of 6,900 total LF; pipe base cost split proportionally from Carollo Weighted Base Cost of Piping Alone ($15,656,100); actual blended $/LF = $2,269/LF vs Carollo baseline $2,850. 17% gravity / 83% LPS; affluent coastal Black Point/Kahala area; high groundwater | Component_Estimated | None | None
Hauula-Kaipapau | Oahu | Carollo | 2026 | Collection | Gravity Main | 27937 | LF | 77860419 |  | 2787 | Carollo Draft 2026 EPA Grant County Studies | Gravity collection (27,937 LF; 91% of 30,700 total LF; pipe base cost split proportionally from Carollo Weighted Base Cost of Piping Alone ($85,560,900); actual blended $/LF = $2,787/LF vs Carollo baseline $2,850. Decentralized; new WWTP; 91% gravity / 9% LPS; WWTP $156,852/conn reflects moderate economies of scale | Component_Estimated | None | None
Kaaawa | Oahu | Carollo | 2026 | Collection | Gravity Main | 19300 | LF | 55005000 |  | 2850 | Carollo Draft 2026 EPA Grant County Studies | Gravity collection (19,300 LF; actual blended $/LF = $2,850/LF vs Carollo baseline $2,850. Decentralized; new WWTP; 100% gravity; hard substrate confirmed in project notes; WWTP $193,783/conn | Component_Known | Difficult Substrate | Difficult Substrate | Carollo notes hard/lava substrate; coastal basalt geology
Kawailoa | Oahu | Carollo | 2026 | Collection | Gravity Main | 4000 | LF | 11400000 |  | 2850 | Carollo Draft 2026 EPA Grant County Studies | Gravity collection (4,000 LF; actual blended $/LF = $2,850/LF vs Carollo baseline $2,850. Decentralized; new WWTP; 100% gravity; smallest decentralized project; highest WWTP $/conn ($268,000) due to diseconomies of scale | Component_Known | None | None
[9 empty] | Carolo Project Average | 2577.1146 |  |  |  |  | Note All Craolo costs averaged into one so the dont disproportionaltely bring eh mean atrificially high
AECOM Puna 8in Gravity Main Unit Cost | Hawaii | AECOM | 2023 | Collection | Gravity Main |  |  |  |  | 1600 | AECOM Puna Wastewater Master Plan Oct 2023 | AECOM-derived 8 in. gravity main unit cost for Hawaii Island lava substrate; lower-bound calibration reference. VERIFIED 2026-06-11 against AECOM Puna WW Facilities Plan Final (Oct 2023) Appendix G-2 "Summary of Estimated Construction Cost Per Foot": 8-inch gravity = $1,600/LF, derived from COH Lono Kona Jan 2018 bid ($1,617 normalized). Published unit cost ($/LF) carried directly in Unit_Cost; Quantity/Total_Cost intentionally blank (this is a published rate, not a project). Resolves the red-flagged "1 LF". Local copy: source_docs/AECOM_Puna_WW_Facilities_Plan_Final_2023.pdf | Component_Known | Difficult Substrate | Difficult Substrate | AECOM confirms lava/basalt substrate throughout Puna district; large-scale economy of scale not representative of small projects | https://github.com/cshuler/WW_Overlay_2024/blob/391927d75b4638b3eb3eb063dfce94182cc62e40/Document_Archive/Cost_Estimates/Puna_District_Wastewater/Puna%20WW%20Fac%20Plan_Final.pdf
Kaiola Place Sewer Extension | Maui | Maui County | 2026 | Collection | Gravity Main | 1000 | LF | 1000000 | 8 | 2000 | Maui County FY2026 Appendix C CIP | Most reliable Maui transmission entry per analyst notes; FY2026 cost may be slightly higher ¦ RBL 2026-06-11: Connections corrected 2500→8 per FY2026 Appendix C CBS-5032 ("~1,000 feet of 8-inch sewer along Kaiola Place to connect eight existing lots"); 2500 appeared copied from Kihei WWPS rows. Quantity 1,000 LF and $1.0M verified. Unit cost x2 applied 2026-06-11 for consistency with rows 22-23 (same FY2026 CIP source; county acknowledges CIP costs understated ~2x): $1,000/LF -> $2,000/LF effective. Source: https://www.mauicounty.gov/DocumentCenter/View/152284/007---FY-2026-Appendix-C-CIP-Description | Component_Known | None | None |  | https://github.com/cshuler/WW_Overlay_2024/blob/f64f71b5e333cd59555ed631a22ffba0cf841fb8/Document_Archive/Cost_Estimates/Maui%20FY2026%20Budget/Maui_County_FY2026_Adopted_Budget.pdf
Upper Waiko Road Sewer Extension | Maui | Maui County | 2026 | Collection | Gravity Main | 2400 | LF | 2000000 | 29 | 1666.6667 | Maui County FY2026 Appendix C CIP + mauinow | From CIP Budget, Maui County Aacknowledges costs should be doubled ¦ RBL 2026-06-11: Verified FY2026 Appendix C CBS-3204 — 2,400 LF, 29 homes, $2.0M. Source: https://www.mauicounty.gov/DocumentCenter/View/152284/007---FY-2026-Appendix-C-CIP-Description |  |  |  |  | https://github.com/cshuler/WW_Overlay_2024/blob/f64f71b5e333cd59555ed631a22ffba0cf841fb8/Document_Archive/Cost_Estimates/Maui%20FY2026%20Budget/Maui_County_FY2026_Adopted_Budget.pdf
Waiko Road Subdivision Sewer System | Maui | Maui County | 2026 | Collection | Gravity Main | 3000 | LF | 2500000 | 75 | 1666.6667 | Maui County FY2026 Appendix C CIP + mauinow | From CIP Budget, Maui County Aacknowledges costs should be doubled ¦ RBL 2026-06-11: Verified FY2026 Appendix C CBS-1158 — 3,000 LF, ~75 lots, $2.5M. Duplicate of Project Total row 125. Source: https://www.mauicounty.gov/DocumentCenter/View/152284/007---FY-2026-Appendix-C-CIP-Description |  |  |  |  | https://github.com/cshuler/WW_Overlay_2024/blob/f64f71b5e333cd59555ed631a22ffba0cf841fb8/Document_Archive/Cost_Estimates/Maui%20FY2026%20Budget/Maui_County_FY2026_Adopted_Budget.pdf
[9 empty] | Mean | 1902.0896
[9 empty] | Median | 1666.6667
Project_Name | Island | Source_Org | Dollar_Year | Component_Group | Component_Type | Quantity | Quantity_Unit | Total_Cost | Connections | Unit_Cost | Citation | Notes | Cost_Basis | Complicating_Factor_Collection | Complicating_Factor_Conveyance | Factor_Note
Kipuka St | Kauai | Carollo | 2026 | Conveyance | Force Main | 4300 | LF | 12255000 |  | 2850 | Carollo Draft 2026 EPA Grant County Studies | Force main (4,300 LF) to Poipu WRF; cost is residual of pipe base after collection portion; priced at Carollo gravity baseline so treat cautiously. WWPS cost is buried in additional costs ($25.3M) and not separable. | Component_Estimated | None | None
Nawiliwili Rd | Kauai | Carollo | 2026 | Conveyance | Force Main | 3900 | LF | 8385000 |  | 2150 | Carollo Draft 2026 EPA Grant County Studies | Force main (3,900 LF) to Lihue-Puhi WRF; cost is residual of pipe base after collection; priced at LPS baseline rate. WWPS cost buried in additional costs ($17.4M). | Component_Estimated | None | None
AECOM Puna 12in+ Trunk Main Unit Cost | Hawaii | AECOM | 2023 | Conveyance | Trunk Main |  |  |  |  | 3700 | AECOM Puna Wastewater Master Plan Oct 2023 | AECOM-derived 12 in.+ trunk/interceptor unit cost; large-diameter gravity conveyance benchmark for Hawaii Island hard substrate ¦ VERIFIED 2026-06-11: AECOM Appendix G-2 table, 12-inch gravity = $3,700/LF. Local copy: source_docs/AECOM_Puna_WW_Facilities_Plan_Final_2023.pdf Quantity/Total_Cost blanked 2026-06-11 - published rate, not a project (same treatment as row 20). | Component_Known | Difficult Substrate | Difficult Substrate | Puna district lava substrate; represents upper end of normal conveyance range for Hawaii Island conditions | https://github.com/cshuler/WW_Overlay_2024/blob/391927d75b4638b3eb3eb063dfce94182cc62e40/Document_Archive/Cost_Estimates/Puna_District_Wastewater/Puna%20WW%20Fac%20Plan_Final.pdf
Hale Hālāwai Force Main Replacement | Hawaii | Alpha Construction | 2025 | Conveyance | Force Main | 900 | LF | 6451304 |  | 7168.1156 | Public Bid April 2025; Alpha Construction | 12 in. force main; hard substrate Hawaii Island; upper-bound benchmark for large-diameter conveyance ($7,168/LF); public bid April 2025 ¦ RBL 2026-06-11: Verified — Hawaii County DEM and Oct 2025 news confirm $6.4M, 12-in force main, AOC-required; DOH EA exemption 80-30 (2024). Length 900 LF not independently re-verified. | Component_Known | Difficult Substrate | Difficult Substrate | Hawaii Island hard/lava substrate confirmed; public bid provides reliable unit cost benchmark | https://github.com/cshuler/WW_Overlay_2024/blob/529ca680db501c488c879d202f8e942304020ac9/Document_Archive/Cost_Estimates/Hale%20Halawai/Sewer%20Force%20Main%20Replacement%20Project%20in%20Kailua-Kona%20Starts%20Oct.pdf
Kihei No. 6 Force Main Replacement | Maui | Maui County | 2026 | Conveyance | Force Main | 4289 | LF | 6000000 | 2500 | 2797.855 | Maui County FY2026 Appendix C CIP | Sewer line replacement; FY2026 funding only; actual cost likely higher ¦ Salvaged 2026-06-11 per 6/4 meeting: unit cost x2 (county-acknowledged CIP underestimate), $1,399 -> $2,798/LF. FY2026 Appendix C CBS-2729 (appropriation $1.0M; project total $6M retained): https://www.mauicounty.gov/DocumentCenter/View/152284/007---FY-2026-Appendix-C-CIP-Description | Component_Estimated | None | None
Dowsett Highlands Relief Sewer | Oahu | CCH-ENV | 2018 | Conveyance | Relief Sewer (Open Trench Urban) | 5500 | LF | 21262410 |  | 3865.8927 | Bid total for W5-17 RFB-ENV-1130909 (Nuuanu Avenue contract - open trench). | All-in unit cost for open-trench urban sewer installation. Length derived by documented geographic measurement in extraction notes. Added in v3 quick-method. | Component_Estimated | None | None | Length derived by documented geographic measurement cross-check.
Dowsett Highlands Relief Sewer | Oahu | CCH-ENV | 2018 | Conveyance | Relief Sewer (Guided Bore Urban) | 8780 | LF | 41850192 |  | 4766.5367 | Bid total for W6-17 RFB-ENV-1131504 (Pali Highway contract - primarily guided bore). | All-in unit cost for guided-bore urban sewer installation. Length derived as PER total minus W5-17 measured length. Added in v3 quick-method. | Component_Estimated | None | Difficult Substrate | Length derived by documented geographic measurement cross-check; guided-bore premium context.
Kihei No. 8 Force Main Replacement | Maui | Maui County | 2022 | Conveyance | Force Main | 2000 | LF | 2125000 |  | 1062.5 | DOH Section 106 publication CWSRF C150077-28 (2022-03-23); PER 2021-12-14 Sec 3.3 (2,000 LF); SRF P7728 extraction | Restored 2026-06-12 (RL): awarded force-main replacement contract unit cost. Unit cost is low relative to other conveyance rows because replacement runs in the existing pipe corridor, so excavation and alignment work is far easier than new construction. Included per 6/4 meeting direction to salvage real data points where defensible (the workbook substrate/terrain factors already cover part of the new-construction difficulty difference). | Component_Known | None | None
Kihei No. 7 Force Main Replacement | Maui | Maui County | 2022 | Conveyance | Force Main | 1550 | LF | 2096575 |  | 1352.629 | DOH Section 106 publication CWSRF C150077-32 (2022-03-23); PER 2021-12-17 Sec 3.3 (1,550 LF); SRF P7732 extraction | Restored 2026-06-12 (RL): awarded force-main replacement contract unit cost. Unit cost is low relative to other conveyance rows because replacement runs in the existing pipe corridor, so excavation and alignment work is far easier than new construction. Included per 6/4 meeting direction to salvage real data points where defensible (the workbook substrate/terrain factors already cover part of the new-construction difficulty difference). | Component_Known | None | None
[9 empty] | Mean | 3301.5032
[9 empty] | Median | 2850
Project_Name | Island | Source_Org | Dollar_Year | Component_Group | Component_Type | Quantity | Quantity_Unit | Total_Cost | Connections | Unit_Cost | Citation | Notes | Cost_Basis | Complicating_Factor_Collection | Complicating_Factor_Conveyance | Factor_Note
Kihei WWPS No. 7 Relocation | Maui | Maui County | 2026 | Pump | Regional Pump Station | 1 | EA | 9400000 | 2500 | 9400000 | Maui County FY2026 Appendix C CIP | 1.5 MGD capacity; ~2,500 homes served; conservatively estimated from FY2026 CIP Appendix C ¦ CWSRF SFY2027 draft C150077-36 separately lists Kihei WWPS No. 7 Relocation at $11.9M; retained the $9.4M local CIP value to avoid overwriting the established source chain, but the CWSRF figure supports the same order of magnitude. | Component_Estimated | None | None
Kihei WWPS No. 4 Modification | Maui | Maui County | 2026 | Pump | Regional Pump Station | 1 | EA | 4000000 |  | 4000000 | Maui County FY2026 Appendix C CIP | Described as essentially a new pump station despite modification label in CIP Excluded from generic neighborhood-pump derivation in v8 because this appears too large/complex for a typical neighborhood pump planning proxy. | Component_Estimated | None | None
Kihei WWPS No. 6 Modification/Upgrade | Maui | Maui County | 2026 | Pump | Regional Pump Station | 1 | EA | 7800000 |  | 7800000 | Maui County FY2026 Appendix C CIP | FY2026 CIP cost only Excluded from generic neighborhood-pump derivation in v8 because this appears too large/complex for a typical neighborhood pump planning proxy. ¦ Resolved 2026-06-11: FY2026 Appendix C CBS-3569 shows $1.0M FY2026 appropriation only; $7.8M retained as project total (higher-figure convention). | Component_Estimated | None | None
Kehalani Pump Station | Maui | Hawaii CWSRF / Maui County | 2027 | Pump | Regional Pump Station | 1 | EA | 9000000 |  | 9000000 | Hawaii CWSRF SFY2027 draft IUP C150052-68; Maui FY2026 Appendix C CBS-6083 | Added 2026-06-12 (RL): CWSRF SFY2027 draft lists Kehalani Pump Station at $9.0M. Maui FY2026 Appendix C lists $1.6M and describes a new pump station plus force main to Central Maui WWRF; separate CWSRF line C150052-72 lists Kehalani Force Main and Gravity Sewer at $16.8M, so $9.0M is used here as the pump-station project total rather than a current-year appropriation.
Hanapepe Fire Station SPS Upgrade | Kauai | Hawaii CWSRF | 2027 | Pump | Regional Pump Station | 1 | EA | 4500000 |  | 4500000 | Hawaii CWSRF SFY2027 draft IUP C150050-18 | Added 2026-06-12 (RL): CWSRF SFY2027 draft lists station-specific SPS upgrade at $4.5M. Used as a Hawaii pump-station upgrade benchmark, not a clean new-station construction cost; scope should be verified if later documentation separates equipment, civil, electrical, or force-main work.
Hanapepe River Side SPS Upgrade | Kauai | Hawaii CWSRF | 2027 | Pump | Regional Pump Station | 1 | EA | 4500000 |  | 4500000 | Hawaii CWSRF SFY2027 draft IUP C150050-17 | Added 2026-06-12 (RL): CWSRF SFY2027 draft lists station-specific SPS upgrade at $4.5M. Used as a Hawaii pump-station upgrade benchmark, not a clean new-station construction cost; scope should be verified if later documentation separates equipment, civil, electrical, or force-main work.
Neighborhood Pump Station (Street-Scale) — EPA 2022 CWNS Planning Estimate | Hawaii | EPA / WRRC planning estimate | 2022 | Pump Station | Neighborhood Pump Station | 1 | EA | 750000 |  | 750000 | EPA 2022 Clean Watersheds Needs Survey Cost Estimation Tool Methods, Equation 3-2: Cost = n × $423,184 × C_MGD + $499,364 (2022 national dollars). Hawaii Oahu location factor ~1.40× applied to national base. Source: https://www.epa.gov/system/files/documents/2024-05/2022-cwns-cost-estimation-tool-methods.pdf | EPA 2022 national base at 0.05–0.10 MGD ≈ $521K–$542K. × 1.40 Hawaii-Oahu RSMeans location factor → ~$729K–$759K. Rounded to $750K for planning. Fixed term ($499K) dominates at small scales; capacity term adds ~$21K per 0.05 MGD. Appropriate for street-scale stations serving 50–150 homes pumping uphill. Outer-island premium may apply (1.5× or higher vs. national). | Engineer_Estimate |  |  | EPA 2022 CWNS Eq 3-2 national base × 1.4 Hawaii location factor; 2022 dollars
Regional Pump Station
[9 empty] | Mean | 6533333.333
[9 empty] | Median | 6150000
Neighborhood Pump Station
[9 empty] | Mean | 750000
[9 empty] | Median | 750000
Project_Name | Island | Source_Org | Dollar_Year | Component_Group | Component_Type | Quantity | Quantity_Unit | Total_Cost | Connections | Unit_Cost | Citation | Notes | Cost_Basis | Complicating_Factor_Collection | Complicating_Factor_Conveyance | Factor_Note
Kawailoa | Oahu | Carollo | 2026 | Treatment | WWTP New | 100 | Connections | 26800000 | 100 | 268000 | Carollo Draft 2026 EPA Grant County Studies | New WWTP cost only; $268,000/conn; Decentralized; new WWTP; 100% gravity; smallest decentralized project; highest WWTP $/conn ($268,000) due to diseconomies of scale | Component_Known | None | None
Kaaawa | Oahu | Carollo | 2026 | Treatment | WWTP New | 226 | Connections | 43795000 | 226 | 193783.1858 | Carollo Draft 2026 EPA Grant County Studies | New WWTP cost only; $193,783/conn; Decentralized; new WWTP; 100% gravity; hard substrate confirmed in project notes; WWTP $193,783/conn | Component_Known | Difficult Substrate | Difficult Substrate
Pupukea | Oahu | Carollo | 2026 | Treatment | WWTP New | 665 | Connections | 78225000 | 665 | 117631.5789 | Carollo Draft 2026 EPA Grant County Studies | New WWTP cost only; $117,632/conn; Decentralized; new WWTP; 100% LPS; lowest WWTP $/conn ($117,632) due to economies of scale | Component_Known | None | None
Hauula-Kaipapau | Oahu | Carollo | 2026 | Treatment | WWTP New | 750 | Connections | 117639100 | 750 | 156852.1333 | Carollo Draft 2026 EPA Grant County Studies | New WWTP cost only; $156,852/conn; Decentralized; new WWTP; 91% gravity / 9% LPS; WWTP $156,852/conn reflects moderate economies of scale | Component_Known | None | None
AECOM Puna Cluster Plant (15,000 gpd) | Hawaii | AECOM | 2026 | Treatment | WWTP New | 20.6897 | Connections | 2209091 | 20.6897 | 106772.7317 | AECOM Puna WW Facilities Plan Final (Oct 2023), Sec 7.2.1.3 + Appendix G-2 (basis: Kapoho feasibility study + built Puna Kai Shopping Center WWTP; vendor quotes Apr 2023) | Added 2026-06-12 (RL/Kai): $2.0M (2023$) escalated x1.1045 (AECOM LCC escalation 3.37%/yr, 2023->2026). Equivalent connections = 15,000 gpd / 725 gpd per connection (workbook convention, see row 68). NO conceptual-realization adjustment: cluster costs are vendor-quote/built-project based, unlike the conceptual $40/gal centralized basis (row 69). | Component_Known | None | None | Equivalent connections = 15,000 gpd / 725 gpd per connection = 20.69.
AECOM Puna Cluster Plant (250,000 gpd breakeven) | Hawaii | AECOM | 2026 | Treatment | WWTP New | 344.8276 | Connections | 13254544 | 344.8276 | 38438.1776 | AECOM Puna WW Facilities Plan Final (Oct 2023), Sec 7.2.1.3 + Appendix G-2 ($10M plant @ $40/gal + $2M odor control/buffer; 250,000 gpd = industry breakeven cluster vs in-ground WWTP) | Added 2026-06-12 (RL/Kai): $12.0M (2023$) escalated x1.1045 = $13.25M. Equivalent connections = 250,000 gpd / 725. NO conceptual-realization adjustment (same rationale as row 64). | Component_Known | None | None | Equivalent connections = 250,000 gpd / 725 gpd per connection = 344.83.
[9 empty] | Mean | 146912.9679
Central Maui WWRF (Waikapu) - Equivalent Connections Basis | Maui | County of Maui / public FEIS-era reporting | 2026 | Treatment | WWTP New | 5517.2414 | Connections | 420000000 | 5517.2414 | 76125 | Capacity: County of Maui CDBG-DR Action Plan; Cost: Maui Now Mar. 3 2026. Equivalent connections derived using 725 gpd/connection workbook assumption. Revised cost: Maui Now Apr 24 2026 (DEM forecast $298M-$420M) https://mauinow.com/2026/04/24/waikapu-sewer-plant-costs-more-than-double-as-maui-council-considers-9-sewer-fee-hike/ | Connection-based treatment row added so Central Maui can participate in workbook derivation. Derived from the 4.0 MGD public planning estimate using 725 gpd/connection workbook assumption; not a stated homes-served count. Renamed in v5 for clarity. ¦ Updated 2026-06-11: Total_Cost revised $130.6M (FEIS planning level) to $420M per Maui DEM forecast $298M-$420M (high end adopted per higher-figure convention; original 2022 conceptual estimate lacked geotech/survey/equipment quotes, pre-wildfire). Sole input to Medium WWTP tier (K67). | Component_Estimated | None | None | Derived equivalent connections = 4.0 MGD / 0.000725 MGD per connection = 5517.24.
AECOM Puna Centralized WWTP @ Subregional Scale (1.5 MGD) - Adjusted | Hawaii | AECOM | 2026 | Treatment | WWTP New | 2068.9655 | Connections | 192955590 | 2068.9655 | 93261.8685 | AECOM Puna WW Facilities Plan Final (Oct 2023), Sec 7.2.1.3 + Appendix G-2 ($40/gallon treated capacity, R-1 treatment, 2023$, from "similar previous projects") | Added 2026-06-12 (RL/Kai). METHODOLOGY: AECOM conceptual $40/gal (2023$) not trusted as-is — same planning-level vintage as Central Maui 2022 conceptual $130.6M that realized to $420M (2026 DEM forecast). Applied the SAME realization factor as Central Maui: x3.216 ($420M/$130.6M). RL recalled ~2x; actual is 3.22x. Vintage caveat: factor base year 2022 vs AECOM 2023 — carries ~1 extra year of escalation (conservative-high ~3%). Adjusted $128.6M/MGD x 1.5 MGD (Alt 2 subregional scale: 6 MGD / 4 plants) = $192.96M. Equivalent connections = 1.5 MGD / 725 gpd = 2,068.97 -> $93,262/conn. Raw unadjusted: $44.2M/MGD 2026$ = $32,032/conn. | Component_Estimated | None | None | Equivalent connections = 1.5 MGD / 0.000725 MGD per connection = 2068.97.
Hilo WWTP Improvement Project (Awarded Contract) | Hawaii | County of Hawaii DEM | 2025 | Treatment | WWTP Upgrade | 6896.5517 | Connections | 337000000 | 6896.5517 | 48865 | Big Island Now 2025-08-01 (groundbreaking, $337M Nan Inc contract) https://bigislandnow.com/2025/08/01/long-awaited-improvement-project-to-hilo-wastewater-treatment-plant-begins-this-month/ ; Wastewater Digest press release; Hawaii Tribune-Herald 2025-08-01; EPA AOC March 2024 | Added 2026-06-12 (RL/Kai): $337M awarded construction contract (Nan Inc., completion 2030) — new headworks, primary+secondary treatment upgrades, solids handling, odor control, electrical/controls. Awarded-bid basis -> NO conceptual-realization adjustment (x3.216 factor is for conceptual estimates only, see AECOM row methodology). DENOMINATOR per RL 2026-06-12: same design-capacity convention as Sand Island and Central Maui — design ~5.0 MGD (AECOM Puna Facilities Plan: Hilo expansion "11 MGD total" = 5 existing + 6 Puna; news states 3 MGD average flow serving ~30,000 residents). 5 MGD / 725 gpd = 6,896.6 equiv conn -> $48,865/conn. Alt basis (3 MGD avg flow): $81,446/conn — noted for sensitivity. Medium tier by connections (<10,000). | Component_Known | None | None | Equivalent connections = 5.0 MGD design / 0.000725 MGD per connection = 6896.55. Design capacity inferred from AECOM Puna plan (11 - 6 = 5 MGD existing); avg flow 3 MGD per county/news.
[9 empty] | Mean | 72750.6228
Sand Island WWTP Ph1 Secondary - MBR (ENR Contract) | Oahu | CCH ENV / Hensel Phelps / ENR | 2022 | Treatment | WWTP Upgrade | 27580 | Connections | 417000000 | 27580 | 15120 | ENR Feb 2025 https://www.enr.com/articles/58801; CCH ENV https://www.honolulu.gov/env/sand-island-wwtp-projects/ | Phase 1 MBR secondary treatment upgrade; 20 MGD capacity. Equiv. connections = 20 MGD / 0.000725 MGD per conn = 27,580. Construction contract value $417M per ENR; NTP Dec 2021. Unit cost $15,120/conn. Large centralized urban upgrade — strong economy of scale. NOT comparable to small standalone WWTP New/Upgrade benchmarks in this dataset. Retained in Large-tier derivation (K72), team decision 2026-06-11. | Component_Known | None | None | Retrofit of existing 24-acre urban facility under severe space constraints. MBR technology selected partly for compact footprint. Dollar_Year = 2022 (NTP / early construction).
Sand Island WWTP Ph1 Secondary - MBR (ENV NTP Value) | Oahu | CCH ENV | 2022 | Treatment | WWTP Upgrade | 27580 | Connections | 460000000 | 27580 | 16680 | CCH ENV Mayor ENV Summary https://www.rickblangiardi.com/department-of-environmental-services/; CCH ENV https://www.honolulu.gov/env/sand-island-wwtp-projects/ | Phase 1 MBR secondary treatment; ENV-reported NTP program value $460M vs. contractor-reported $417M; difference reflects design, engineering, and contingency costs. Unit cost $16,680/conn. Dollar_Year = 2022. Retained in Large-tier derivation (K72), team decision 2026-06-11. | Component_Known | None | None | ENV-reported program value; higher than Hensel Phelps construction contract due to design and program management costs included in NTP value.
Sand Island WWTP Full Secondary Upgrade Ph1+Ph2 (Official Aggregate) | Oahu | CCH ENV | 2025 | Treatment | WWTP Upgrade | 124110 | Connections | 2500000000 | 124110 | 20145 | CCH ENV Budget Presentation to City Council Budget Committee March 4 2025 https://www.honolulu.gov/env/wp-content/uploads/sites/29/2025/03/BUDGET-Presentation-3-4-25-Sewer-Rate-Increase.pdf | Full secondary treatment upgrade Phases 1+2; 90 MGD total / 0.000725 MGD per conn = 124,110 equiv. connections. Approximate Cost = $2.5B per ENV Budget Presentation slide 17 (March 2025); most official single-source aggregate figure. Includes MBR Phase 1 (20 MGD) + AGS Phase 2 (70 MGD) + associated solids and site work. Unit cost $20,145/conn. Hawaii-embedded construction costs including consent decree compliance features. Retained in Large-tier derivation (K72), team decision 2026-06-11. | Component_Known | None | None | Official ENV estimate per March 2025 sewer rate increase budget presentation. 2035 completion deadline per 2010 Consent Decree. Phase 2 EIS (EISPN published Jan 2026) will provide more granular Phase 2 cost detail when Draft EIS is released.
Honouliuli WWTP Secondary Treatment Program Ph 1B+1C+1D (Awarded Bids) | Oahu | CCH-ENV | 2024 | Treatment | WWTP Upgrade | 34482.7586 | Connections | 783687106 | 34482.7586 | 22726.9261 | CCH-ENV PER 2020-07-10 Table ES-4 (Ph 1B awarded bid $267M, 2024); CCH-ENV contract CT-ENV-2300272 $516,687,105.50 (2023, Ph 1C+1D per extraction notes). SRF P5182 extraction: /src/hcpt_overlay_cost_model/data/extraction_rounds/2026-05-11_round2/3_P5182/ | Added 2026-06-12 (RL/Kai): second Large-tier facility (Sand Island was sole source). Awarded-bid basis -> NO conceptual-realization adjustment (x3.216 factor applies only to planning-level conceptual estimates, see row 69 methodology). Scope: upgrade to FULL secondary at HLIWWTP — PER states primary capacity 38 MGD, secondary 13 MGD -> increment 25 MGD. $267M (1B) + $516.687M (1C+1D contract) = $783.687M / 25 MGD = $31.3M/MGD; equivalent connections 25 MGD / 725 gpd = 34,482.8 -> $22,727/conn. Excludes Ph 1A $68M sludge drying (solids stream, not capacity). Caveats: contract-to-phase mapping (1C+1D) per SRF extraction notes ("likely"); mixed dollar years 2023/2024 not escalated. | Component_Known | None | None | Equivalent connections = 25 MGD secondary increment / 0.000725 MGD per connection = 34,482.76.
[9 empty] | Mean | 18667.9815
Cost Model Validation data from Carollo.
Project_Name | Island | Source_Org | Dollar_Year | Component_Group | Component_Type | Quantity | Quantity_Unit | Total_Cost | Connections | Unit_Cost | Citation | Notes | Cost_Basis | Complicating_Factor_Collection | Complicating_Factor_Conveyance | Factor_Note | Validation_Scope | Validation Project Type
Kiahuna Golf Course | Kauai | Carollo | 2026 | Project Total | Bundled / Not Separated | 81 | Connections | 15200000 | 81 | 187654.321 | Carollo Draft 2026 EPA Grant County Studies | 100% gravity; connects to Poipu WRF; minimal additional costs ($95K) ¦ PROJECT TOTAL validation reference — do not use for unit cost calibration | Project_Bundled | None | None |  | Collection only | 1
Hoona Rd | Kauai | Carollo | 2026 | Project Total | Bundled / Not Separated | 77 | Connections | 8900000 | 77 | 115584.4156 | Carollo Draft 2026 EPA Grant County Studies | 100% LPS; connects to Poipu WRF; lowest actual $/LF in Carollo dataset ($1,978/LF) ¦ PROJECT TOTAL validation reference — do not use for unit cost calibration | Project_Bundled | None | None |  | Collection only | 1
Puhi | Kauai | Carollo | 2026 | Project Total | Bundled / Not Separated | 313 | Connections | 39700000 | 313 | 126837.0607 | Carollo Draft 2026 EPA Grant County Studies | 10% gravity / 90% LPS; multiple diameters (4, 8, 12 in.); connects to Lihue-Puhi WRF ¦ PROJECT TOTAL validation reference — do not use for unit cost calibration | Project_Bundled | None | None |  | Collection only | 1
Pukalani | Maui | Carollo | 2026 | Project Total | Bundled / Not Separated | 1519 | Connections | 247300000 | 1519 | 162804.4766 | Carollo Draft 2026 EPA Grant County Studies | 42% gravity / 58% LPS; largest private project by connections; trunk line premium (12-18 in. diameters) ¦ PROJECT TOTAL validation reference — do not use for unit cost calibration | Project_Bundled | None | None |  | Collection only | 1
Aiea Heights | Oahu | Carollo | 2026 | Project Total | Bundled / Not Separated | 130 | Connections | 13200000 | 130 | 101538.4615 | Carollo Draft 2026 EPA Grant County Studies | 100% LPS; 4 in. single diameter; low additional costs ($730K) ¦ PROJECT TOTAL validation reference — do not use for unit cost calibration | Project_Bundled | None | None |  | Collection only | 1
Ewa | Oahu | Carollo | 2026 | Project Total | Bundled / Not Separated | 978 | Connections | 95900000 | 978 | 98057.2597 | Carollo Draft 2026 EPA Grant County Studies | 100% gravity; 8 and 12 in. pipe; additional costs $8.4M may reflect larger diameter pipe premium ¦ PROJECT TOTAL validation reference — do not use for unit cost calibration | Project_Bundled | None | None |  | Collection only | 1
Kahaluu | Oahu | Carollo | 2026 | Project Total | Bundled / Not Separated | 166 | Connections | 46100000 | 166 | 277710.8434 | Carollo Draft 2026 EPA Grant County Studies | 85% gravity / 15% LPS; dispersed layout; high LF/conn ratio (108 LF/conn); actual blended $/LF ($2,575) below weighted baseline ($2,745) ¦ PROJECT TOTAL validation reference — do not use for unit cost calibration | Project_Bundled | None | None |  | Collection only | 1
Ahuimanu | Oahu | Carollo | 2026 | Project Total | Bundled / Not Separated | 133 | Connections | 15900000 | 133 | 119548.8722 | Carollo Draft 2026 EPA Grant County Studies | 7% gravity / 93% LPS; actual blended $/LF ($2,038) lowest among all public extensions; below weighted baseline ($2,199) ¦ PROJECT TOTAL validation reference — do not use for unit cost calibration | Project_Bundled | None | None |  | Collection only | 1
Kailua | Oahu | Carollo | 2026 | Project Total | Bundled / Not Separated | 173 | Connections | 18400000 | 173 | 106358.3815 | Carollo Draft 2026 EPA Grant County Studies | 100% gravity; coastal peninsula; compact layout (35 LF/conn); modest additional costs ($1.3M) ¦ PROJECT TOTAL validation reference — do not use for unit cost calibration | Project_Bundled | None | None |  | Collection only | 1
Makaha | Oahu | Carollo | 2026 | Project Total | Bundled / Not Separated | 107 | Connections | 15600000 | 107 | 145794.3925 | Carollo Draft 2026 EPA Grant County Studies | 34% gravity / 66% LPS; linear beachfront along Farrington Hwy; actual $/LF ($2,197) below baseline ($2,388) ¦ PROJECT TOTAL validation reference — do not use for unit cost calibration | Project_Bundled | None | None |  | Collection only | 1
Kaupuni | Oahu | Carollo | 2026 | Project Total | Bundled / Not Separated | 181 | Connections | 19200000 | 181 | 106077.3481 | Carollo Draft 2026 EPA Grant County Studies | 55% gravity / 45% LPS; infill project; two non-contiguous cesspool clusters in Waianae Valley ¦ PROJECT TOTAL validation reference — do not use for unit cost calibration | Project_Bundled | None | None |  | Collection only | 1
Waimanalo Beach | Oahu | Carollo | 2026 | Project Total | Bundled / Not Separated | 284 | Connections | 40500000 | 284 | 142605.6338 | Carollo Draft 2026 EPA Grant County Studies | 100% gravity; linear beachfront; multiple connection points along Kalanianaole Hwy ¦ PROJECT TOTAL validation reference — do not use for unit cost calibration | Project_Bundled | None | None |  | Collection only | 1
Kaimuki | Oahu | Carollo | 2026 | Project Total | Bundled / Not Separated | 76 | Connections | 6900000 | 76 | 90789.4737 | Carollo Draft 2026 EPA Grant County Studies | 22% gravity / 78% LPS; smallest public project; urban infill near Diamond Head crater ¦ PROJECT TOTAL validation reference — do not use for unit cost calibration | Project_Bundled | None | None |  | Collection only | 1
Makiki | Oahu | Carollo | 2026 | Project Total | Bundled / Not Separated | 263 | Connections | 52200000 | 263 | 198479.0875 | Carollo Draft 2026 EPA Grant County Studies | 80% gravity / 20% LPS; hillside community Makiki Heights/Round Top; natural slope aids gravity flow ¦ PROJECT TOTAL validation reference — do not use for unit cost calibration | Project_Bundled | None | None |  | Collection only | 1
Diamond Head | Oahu | Carollo | 2026 | Project Total | Bundled / Not Separated | 174 | Connections | 17600000 | 174 | 101149.4253 | Carollo Draft 2026 EPA Grant County Studies | 17% gravity / 83% LPS; affluent coastal Black Point/Kahala area; high groundwater ¦ PROJECT TOTAL validation reference — do not use for unit cost calibration | Project_Bundled | None | None |  | Collection only | 1
[9 empty] | Average | 138732.6302
Kipuka St | Kauai | Carollo | 2026 | Project Total | Bundled / Not Separated | 107 | Connections | 48700000 | 107 | 455140.1869 | Carollo Draft 2026 EPA Grant County Studies | Gravity collection (3,900 LF) + WWPS + force main (4,300 LF) to Poipu WRF; additional costs $25.3M primarily WWPS and FM ¦ PROJECT TOTAL validation reference — do not use for unit cost calibration | Project_Bundled | None | None |  | Collection + WWPS + Force Main | 2
Nawiliwili Rd | Kauai | Carollo | 2026 | Project Total | Bundled / Not Separated | 365 | Connections | 57600000 | 365 | 157808.2192 | Carollo Draft 2026 EPA Grant County Studies | 100% LPS collection (14,800 LF) + WWPS + force main (3,900 LF) to Lihue-Puhi WRF; additional costs $17.4M primarily WWPS and FM ¦ PROJECT TOTAL validation reference | Project_Bundled | None | None |  | Collection + WWPS + Force Main | 2
[9 empty] | Average | 306474.203
Hauula-Kaipapau | Oahu | Carollo | 2026 | Project Total | Bundled / Not Separated | 750 | Connections | 203200000 | 750 | 270933.3333 | Carollo Draft 2026 EPA Grant County Studies | Decentralized; new WWTP; 91% gravity / 9% LPS; WWTP $156,852/conn reflects moderate economies of scale ¦ PROJECT TOTAL validation reference — do not use for unit cost calibration | Project_Bundled | None | None |  | Collection + new WWTP | 3
Kaaawa | Oahu | Carollo | 2026 | Project Total | Bundled / Not Separated | 226 | Connections | 98800000 | 226 | 437168.1416 | Carollo Draft 2026 EPA Grant County Studies | Decentralized; new WWTP; 100% gravity; hard substrate confirmed in project notes; WWTP $193,783/conn ¦ PROJECT TOTAL validation reference — do not use for unit cost calibration | Project_Bundled | Difficult Substrate | Difficult Substrate |  | Collection + new WWTP | 3
Pupukea | Oahu | Carollo | 2026 | Project Total | Bundled / Not Separated | 665 | Connections | 191100000 | 665 | 287368.4211 | Carollo Draft 2026 EPA Grant County Studies | Decentralized; new WWTP; 100% LPS; lowest WWTP $/conn ($117,632) due to economies of scale ¦ PROJECT TOTAL validation reference — do not use for unit cost calibration | Project_Bundled | None | None |  | Collection + new WWTP | 3
Kawailoa | Oahu | Carollo | 2026 | Project Total | Bundled / Not Separated | 100 | Connections | 38200000 | 100 | 382000 | Carollo Draft 2026 EPA Grant County Studies | Decentralized; new WWTP; 100% gravity; smallest decentralized project; highest WWTP $/conn ($268,000) due to diseconomies of scale ¦ PROJECT TOTAL validation reference — do not use for unit cost calibration | Project_Bundled | None | None |  | Collection + new WWTP | 3
[9 empty] | Average | 344367.474
Cost Model vs. Carollo Data Comparison
Infrastructure Configuration | Validation category | Carollo Bundled Project Cost/Connection | Cost Modeled Total Cost/Connection
Collection only | 1 | 138732.6302 | 177632.0634
Collection + WWPS + Force Main | 2 | 306474.203 | 327214.5048
Collection + new WWTP | 3 | 344367.474 | 383949.5206
Collection, Conveyance + WWTPs + pump stations) | 4 | NA | 464856.5762